## Total
Site Name | Day | Month | Year | Total Electricity Kwh | Electricity Tariff ($/Kwh) | Total Fuel Oil (Liters) | Fuel Oil $/Liter | LPG (Kg) | LPG $/Kg | Water Utility Supply (m3) m3 | Water Utility Supply (m3) $/m3 | Irrigation Water (m3) m3 | Irrigation water $/m3 | Room Nights
Beirut | 1 | 5 | 2021 | 8346 | 0.20265 | 195 | 0.92 | 0 | 1.5686 | 7 | 34.5622 | 0 | 0.6 | 0
Beirut | 2 | 5 | 2021 | 6548 | 0.15947 | 153 | 0.92 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 3 | 5 | 2021 | 7179 | 0.16489 | 141 | 0.92 | 0 | 1.5686 | 289 | 0.83715 | 0 | 0.6 | 0
Beirut | 4 | 5 | 2021 | 8383 | 0.23069 | 95 | 0.92 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 5 | 5 | 2021 | 4768 | 0.43179 | 164 | 0.92 | 0 | 1.5686 | 295 | 0.82012 | 0 | 0.6 | 0
Beirut | 6 | 5 | 2021 | 3912 | 0.33343 | 155 | 0.92 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 7 | 5 | 2021 | 8995.4 | 0.24912 | 166 | 0.92 | 0 | 1.5686 | 293 | 0.82572 | 0 | 0.6 | 0
Beirut | 8 | 5 | 2021 | 8249.8 | 0.26949 | 156 | 0.92 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 9 | 5 | 2021 | 9025.8 | 0.22805 | 112 | 0.92 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 10 | 5 | 2021 | 9481 | 0.26188 | 82 | 0.92 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 11 | 5 | 2021 | 9028 | -0.061126 | 137 | 0.94 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 12 | 5 | 2021 | 9411 | 0.30014 | 154 | 0.94 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 13 | 5 | 2021 | 9646 | 0.24392 | 115 | 0.94 | 0 | 1.5686 | 341 | 0.70949 | 0 | 0.6 | 0
Beirut | 14 | 5 | 2021 | 8868 | 0.22466 | 89 | 0.94 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 15 | 5 | 2021 | 7587 | 0.25123 | 139 | 0.94 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 16 | 5 | 2021 | 12839 | 0.27282 | 115 | 0.94 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 17 | 5 | 2021 | 10089 | 0.23295 | 93 | 0.94 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 18 | 5 | 2021 | 10297 | 0.26907 | 136 | 0.94 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 19 | 5 | 2021 | 15339 | 0.18551 | 95 | 0.94 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 20 | 5 | 2021 | 8897 | 0.19633 | 63 | 1.003 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 21 | 5 | 2021 | 10235 | 0.26992 | 209 | 1.003 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 22 | 5 | 2021 | 12191 | 0.3043 | 129 | 1.003 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 23 | 5 | 2021 | 8568 | 0.24375 | 69 | 1.003 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 24 | 5 | 2021 | 13728 | 0.1583 | 211.2 | 1.003 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 25 | 5 | 2021 | 9803 | 0.23926 | 90 | 1.003 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 26 | 5 | 2021 | 14177 | 0.30393 | 114 | 1.003 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 27 | 5 | 2021 | 11827 | 0.26851 | 106 | 1.003 | 0 | 1.5686 | 435 | 0.55617 | 0 | 0.6 | 0
Beirut | 28 | 5 | 2021 | 0 | 0 | 0 | 1.003 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 29 | 5 | 2021 | 0 | 0 | 0 | 1.003 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 30 | 5 | 2021 | 0 | 0 | 0 | 1.003 | 0 | 1.5686 | 0 | 0 | 0 | 0.6 | 0
Beirut | 31 | 5 | 2022 | 0 | 0 | 0 | 1.003 | 0 | 1.5686 | 0 | 0 | 0 | 1.6 | 0

## Submetering
Site Name | Day | Month | Year | ATS1 Kwh | ATS2 Kwh | ATS3 Kwh | ATS4 Kwh | ATS5 Kwh | Guest (m3) | Kitchen & Laundry (m3) | Room Nights
Beirut | 1 | 5 | 2021 | 2194 | 1280 | 882 | 3356 | 634 | 0 | 0 | 0
Beirut | 2 | 5 | 2021 | 1698 | 912 | 692 | 2632 | 614 | 0 | 0 | 0
Beirut | 3 | 5 | 2021 | 1276 | 920 | 804 | 3588 | 591 | 82 | 36 | 0
Beirut | 4 | 5 | 2021 | 1652 | 2336 | 788 | 2984 | 623 | 1 | 0 | 0
Beirut | 5 | 5 | 2021 | 1880 | 1312 | 912 | 0 | 664 | 105 | 0 | 0
Beirut | 6 | 5 | 2021 | 1498 | 924 | 792 | 5767 | 698 | 0 | 0 | 0
Beirut | 7 | 5 | 2021 | 1848 | 1228 | 968 | 4201 | 750.4 | 145 | 0 | 0
Beirut | 8 | 5 | 2021 | 1638 | 1186 | 792 | 3953 | 680.8 | 0 | 32 | 0
Beirut | 9 | 5 | 2021 | 1780 | 1272 | 796 | 4500 | 677.8 | 26 | 11 | 0
Beirut | 10 | 5 | 2021 | 1812 | 3382 | 836 | 2791 | 660 | 0 | 0 | 0
Beirut | 11 | 5 | 2021 | 1774 | 2956 | 906 | 2692 | 700 | 0 | 0 | 0
Beirut | 12 | 5 | 2021 | 1894 | 3444 | 910 | 2489 | 674 | 0 | 0 | 0
Beirut | 13 | 5 | 2021 | 1736 | 4104 | 788 | 2415 | 603 | 0 | 0 | 0
Beirut | 14 | 5 | 2021 | 1296 | 3042 | 748 | 3136 | 646 | 0 | 0 | 0
Beirut | 15 | 5 | 2021 | 1584 | 2474 | 836 | 2032 | 661 | 0 | 0 | 0
Beirut | 16 | 5 | 2021 | 2340 | 5432 | 1032 | 3443 | 592 | 0 | 0 | 0
Beirut | 17 | 5 | 2021 | 2048 | 2824 | 836 | 3701 | 680 | 0 | 0 | 0
Beirut | 18 | 5 | 2021 | 1882 | 3480 | 1684 | 2450 | 801 | 0 | 0 | 0
Beirut | 19 | 5 | 2021 | 2524 | 6644 | 1176 | 3949 | 1046 | 60 | 0 | 0
Beirut | 20 | 5 | 2021 | 1502 | 3922 | 582 | 2418 | 473 | 0 | 0 | 0
Beirut | 21 | 5 | 2021 | 1992 | 4110 | 774 | 2787 | 572 | 0 | 0 | 0
Beirut | 22 | 5 | 2021 | 2186 | 5208 | 846 | 3243 | 708 | 0 | 0 | 0
Beirut | 23 | 5 | 2021 | 1698 | 3084 | 762 | 2306 | 718 | 0 | 0 | 0
Beirut | 24 | 5 | 2021 | 2230 | 6256 | 952 | 3528 | 762 | 0 | 0 | 0
Beirut | 25 | 5 | 2021 | 2102 | 3580 | 876 | 2482 | 763 | 0 | 0 | 0
Beirut | 26 | 5 | 2021 | 2448 | 6608 | 956 | 3437 | 728 | 2 | 0 | 0
Beirut | 27 | 5 | 2021 | 2160 | 5032 | 908 | 2935 | 792 | 71 | 0 | 0
Beirut | 28 | 5 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Beirut | 29 | 5 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Beirut | 30 | 5 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Beirut | 31 | 5 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
.

## ELEC
OOC | Room OCC |  | MDB3 | MDB3/day | EMDB2 | EMDB2/day | EMDB1 | EMDB1/day | MDB2 | mdb2/day | MDB1 | MDB1/Day | Total KWH | KWH/Rooc | Gen MHW | Gen/Day KWH | EDL KWH | CH1 RH | RH | C1h1 power | CH1 Con KWH | CH2 RH | RH | Ch2 power | CH2 Con KWH | CH3 RH | RH | Ch3 power | CH3 Con KWH | RH total | KWH total | AVG chiller KW/Hr
0% | 0 | 2021-04-30 | 32819750 | 3108 | 4009734 | 304 | 17856136 | 765 | 29011666 | 1972 | 24175590 | 1724 | 7873 | 0 | 16972.836 | 4977 | 2896 | 10175 | 0 | 429166 | 0 | 32312 | 5 | 721364 | 825 | 35884 | 3 | 949998 | 560 | 8 | 1385 | 173.125 | -999706
0% | 0 | 2021-05-01 | 32823106 | 3356 | 4010368 | 634 | 17857018 | 882 | 29012946 | 1280 | 24177784 | 2194 | 8346 | 0 | 16976.763 | 3927 | 4419 | 10175 | 0 | 429166 | 0 | 32312 | 0 | 721364 | 0 | 35889 | 5 | 951030 | 1032 | 5 | 1032 | 206.4
0% | 0 | 2021-05-02 | 32825738 | 2632 | 4010982 | 614 | 17857710 | 692 | 29013858 | 912 | 24179482 | 1698 | 6548 | 0 | 16978.759 | 1996 | 4552 | 10175 | 0 | 429166 | 0 | 32312 | 0 | 721364 | 0 | 35891 | 2 | 951609 | 579 | 2 | 579 | 289.5 |  |  | ATS 4 till power meter is for MDB 3 is replaced
0% | 0 | 2021-05-03 | 32829326 | 3588 | 4011573 | 591 | 17858514 | 804 | 29014778 | 920 | 24180758 | 1276 | 7179 | 0 | 16981.779 | 3020 | 4159 | 10175 | 0 | 429166 | 0 | 32312 | 0 | 721364 | 0 | 35896 | 5 | 952602 | 993 | 5 | 993 | 198.6 | -1004651 |  | Emergency | Normal | Total | Deference
0% | 0 | 2021-05-04 | 32832310 | 2984 | 4012196 | 623 | 17859302 | 788 | 29017114 | 2336 | 24182410 | 1652 | 8383 | 0 | 16985.99 | 4211 | 4172 | 10175 | 0 | 429166 | 0 | 32317 | 5 | 722633 | 1269 | 35896 | 0 | 952602 | 0 | 5 | 1269 | 253.8 | -1007025 | 2021-05-04 | 270643 | 409413 | 680056
0% | 0 | 2021-05-05 | 32832310 | 0 | 4012860 | 664 | 17860214 | 912 | 29018426 | 1312 | 24184290 | 1880 | 4768 | 0 | 16991.6 | 5610 | -842 | 10175 | 0 | 429166 | 0 | 32317 | 0 | 722652 | 19 | 35905 | 9 | 954371 | 1769 | 9 | 1788 | 198.6667 | -1014456 | 2021-05-05 | 270643 | 409413 | 680056 | 0
0% | 0 | 2021-05-06 | 32832310 | 0 | 4013558 | 698 | 17861006 | 792 | 29019350 | 924 | 24185788 | 1498 | 3912 | 0 | 16995.082 | 3482 | 430 | 10175 | 0 | 429166 | 0 | 32317 | 0 | 722652 | 0 | 35909 | 4 | 955297 | 926 | 4 | 926 | 231.5 | -1015450 | 2021-05-06 | 274499 | 411324 | 685823 | 5767
0% | 0 | 2021-05-07 | 32836511 | 4201 | 4014308.4 | 750.4 | 17861974 | 968 | 29020578 | 1228 | 24187636 | 1848 | 8995.4 | 0 | 17000.937 | 5855 | 3140.4 | 10175 | 0 | 429166 | 0 | 32317 | 0 | 722652 | 0 | 35917 | 8 | 956869 | 1572 | 8 | 1572 | 196.5 | -1014626.6 | 2021-05-07 | 277740 | 412284 | 690024 | 4201
0% | 0 | 2021-05-08 | 32840464 | 3953 | 4014989.2 | 680.8 | 17862766 | 792 | 29021764 | 1186 | 24189274 | 1638 | 8249.8 | 0 | 17006.446 | 5509 | 2740.8 | 10175 | 0 | 429166 | 0 | 32317 | 0 | 722652 | 0 | 35924 | 7 | 958420 | 1551 | 7 | 1551 | 221.5714 | -1017112.2 | 2021-05-08 | 280877 | 413100 | 693977 | 3953
0% | 0 | 2021-05-09 | 32844964 | 4500 | 4015667 | 677.8 | 17863562 | 796 | 29023036 | 1272 | 24191054 | 1780 | 9025.8 | 0 | 17012.749 | 6303 | 2722.8 | 10175 | 0 | 429166 | 0 | 32317 | 0 | 722652 | 0 | 35932 | 8 | 960238 | 1818 | 8 | 1818 | 227.25 | -1019084.2 | 2021-05-09 | 284469 | 414008 | 698477 | 4500
0% | 0 | 2021-05-10 | 32847755 | 2791 | 4016327 | 660 | 17864398 | 836 | 29026418 | 3382 | 24192866 | 1812 | 9481 | 0 | 17019.087 | 6338 | 3143 | 10175 | 0 | 429166 | 0 | 32325 | 8 | 724713 | 2061 | 35932 | 0 | 960238 | 0 | 8 | 2061 | 257.625 | -1020410 | 2021-05-10 | 286090 | 415178 | 701268 | 2791
0% | 0 | 2021-05-11 | 32850447 | 2692 | 4017027 | 700 | 17865304 | 906 | 29029374 | 2956 | 24194640 | 1774 | 9028 | 0 | 17024.831 | 5744 | 3284 | 10175 | 0 | 429166 | 0 | 32332 | 7 | 726135 | 1422 | 35932 | 0 | 960238 | 0 | 7 | 1422 | 203.1429 | -1021853 | 2021-05-11 | 287725 | 416235 | 703960 | 2692
0% | 0 | 2021-05-12 | 32852936 | 2489 | 4017701 | 674 | 17866214 | 910 | 29032818 | 3444 | 24196534 | 1894 | 9411 | 0 | 17032.1 | 7269 | 2142 | 10175 | 0 | 429166 | 0 | 32341 | 9 | 728306 | 2171 | 35932 | 0 | 960238 | 0 | 9 | 2171 | 241.2222 | -1024547 | 2021-05-12 | 289550 | 416899 | 706449 | 2489
0% | 0 | 2021-05-13 | 32855351 | 2415 | 4018304 | 603 | 17867002 | 788 | 29036922 | 4104 | 24198270 | 1736 | 9646 | 0 | 17038.805 | 6705 | 2941 | 10175 | 0 | 429166 | 0 | 32349 | 8 | 730287 | 1981 | 35932 | 0 | 960238 | 0 | 8 | 1981 | 247.625 | -1025522 | 2021-05-13 | 291124 | 417740 | 708864 | 2415
0% | 0 | 2021-05-14 | 32858487 | 3136 | 4018950 | 646 | 17867750 | 748 | 29039964 | 3042 | 24199566 | 1296 | 8868 | 0 | 17044.19 | 5385 | 3483 | 10175 | 0 | 429166 | 0 | 32354 | 5 | 731328 | 1041 | 35935 | 3 | 960881 | 643 | 8 | 1684 | 210.5 | -1026783 | 2021-05-14 | 292977 | 419023 | 712000 | 3136
0% | 0 | 2021-05-15 | 32860519 | 2032 | 4019611 | 661 | 17868586 | 836 | 29042438 | 2474 | 24201150 | 1584 | 7587 | 0 | 17050.586 | 6396 | 1191 | 10175 | 0 | 429166 | 0 | 32359 | 5 | 732497 | 1169 | 35935 | 0 | 960881 | 0 | 5 | 1169 | 233.8 | -1030324 | 2021-05-15 | 294108 | 419924 | 714032 | 2032
0% | 0 | 2021-05-16 | 32863962 | 3443 | 4020203 | 592 | 17869618 | 1032 | 29047870 | 5432 | 24203490 | 2340 | 12839 | 0 | 17055.611 | 5025 | 7814 | 10175 | 0 | 429166 | 0 | 32370 | 11 | 735160 | 2663 | 35935 | 0 | 960881 | 0 | 11 | 2663 | 242.0909 | -1025368 | 2021-05-16 | 296883 | 420592 | 717475 | 3443
0% | 0 | 2021-05-17 | 32867663 | 3701 | 4020883 | 680 | 17870454 | 836 | 29050694 | 2824 | 24205538 | 2048 | 10089 | 0 | 17065.003 | 9392 | 697 | 10175 | 0 | 429166 | 0 | 32376 | 6 | 736671 | 1511 | 35939 | 4 | 961645 | 764 | 10 | 2275 | 227.5 | -1034412 | 2021-05-17 | 299259 | 421917 | 721176 | 3701
0% | 0 | 2021-05-18 | 32870113 | 2450 | 4021684 | 801 | 17872138 | 1684 | 29054174 | 3480 | 24207420 | 1882 | 10297 | 0 | 17073.79 | 8787 | 1510 | 10175 | 0 | 429166 | 0 | 32387 | 11 | 738782 | 2111 | 35939 | 0 | 961645 | 0 | 11 | 2111 | 191.9091 | -1035295 | 2021-05-18 | 301110 | 422516 | 723626 | 2450
0% | 0 | 2021-05-19 | 32874062 | 3949 | 4022730 | 1046 | 17873314 | 1176 | 29060818 | 6644 | 24209944 | 2524 | 15339 | 0 | 17086.036 | 12246 | 3093 | 10175 | 0 | 429166 | 0 | 32397 | 10 | 740914 | 2132 | 35939 | 0 | 961645 | 0 | 10 | 2132 | 213.2 | -1034409 | 2021-05-19 | 304137 | 423438 | 727575 | 3949
0% | 0 | 2021-05-20 | 32876480 | 2418 | 4023203 | 473 | 17873896 | 582 | 29064740 | 3922 | 24211446 | 1502 | 8897 | 0 | 17093.373 | 7337 | 1560 | 10175 | 0 | 429166 | 0 | 32412 | 15 | 743939 | 3025 | 35939 | 0 | 961645 | 0 | 15 | 3025 | 201.6667 | -1038207 | 2021-05-20 | 305964 | 424029 | 729993 | 2418
0% | 0 | 2021-05-21 | 32879267 | 2787 | 4023775 | 572 | 17874670 | 774 | 29068850 | 4110 | 24213438 | 1992 | 10235 | 0 | 17101.325 | 7952 | 2283 | 10175 | 0 | 429166 | 0 | 32421 | 9 | 745900 | 1961 | 35939 | 0 | 961645 | 0 | 9 | 1961 | 217.8889 | -1039226 | 2021-05-21 | 308024 | 424756 | 732780 | 2787
0% | 0 | 2021-05-22 | 32882510 | 3243 | 4024483 | 708 | 17875516 | 846 | 29074058 | 5208 | 24215624 | 2186 | 12191 | 0 | 17111.872 | 10547 | 1644 | 10175 | 0 | 429166 | 0 | 32435 | 14 | 748409 | 2509 | 35939 | 0 | 961645 | 0 | 14 | 2509 | 179.2143 | -1041693 | 2021-05-22 | 310775 | 425248 | 736023 | 3243
0% | 0 | 2021-05-23 | 32884816 | 2306 | 4025201 | 718 | 17876278 | 762 | 29077142 | 3084 | 24217322 | 1698 | 8568 | 0 | 17117.407 | 5535 | 3033 | 10175 | 0 | 429166 | 0 | 32442 | 7 | 749823 | 1414 | 35939 | 0 | 961645 | 0 | 7 | 1414 | 202 | -1041224 | 2021-05-23 | 312222 | 426107 | 738329 | 2306
0% | 0 | 2021-05-24 | 32888344 | 3528 | 4025963 | 762 | 17877230 | 952 | 29083398 | 6256 | 24219552 | 2230 | 13728 | 0 | 17129.861 | 12454 | 1274 | 10175 | 0 | 429166 | 0 | 32458 | 16 | 752966 | 3143 | 35939 | 0 | 961645 | 0 | 16 | 3143 | 196.4375 | -1044290 | 2021-05-24 | 315305 | 426552 | 741857 | 3528
0% | 0 | 2021-05-25 | 32890826 | 2482 | 4026726 | 763 | 17878106 | 876 | 29086978 | 3580 | 24221654 | 2102 | 9803 | 0 | 17136.036 | 6175 | 3628 | 10175 | 0 | 429166 | 0 | 32465 | 7 | 754541 | 1575 | 35939 | 0 | 961645 | 0 | 7 | 1575 | 225 | -1042904 | 2021-05-25 | 316769 | 427570 | 744339 | 2482
0% | 0 | 2021-05-26 | 32894263 | 3437 | 4027454 | 728 | 17879062 | 956 | 29093586 | 6608 | 24224102 | 2448 | 14177 | 0 | 17149.122 | 13086 | 1091 | 10175 | 0 | 429166 | 0 | 32481 | 16 | 757511 | 2970 | 35939 | 0 | 961645 | 0 | 16 | 2970 | 185.625 | -1047128 | 2021-05-26 | 319879 | 427897 | 747776 | 3437
0% | 0 | 2021-05-27 | 32897198 | 2935 | 4028246 | 792 | 17879970 | 908 | 29098618 | 5032 | 24226262 | 2160 | 11827 | 0 | 17158.558 | 9436 | 2391 | 10175 | 0 | 429166 | 0 | 32492 | 11 | 760371 | 2860 | 35939 | 0 | 961645 | 0 | 11 | 2860 | 260 | -1046612 | 2021-05-27 | 322078 | 428633 | 750711 | 2935
0% | 0 | 2021-05-28 | 32897198 | 0 | 4028246 | 0 | 17879970 | 0 | 29098618 | 0 | 24226262 | 0 | 0 | 0 | 17158.558 | 0 | 0 | 10175 | 0 | 429166 | 0 | 32492 | 0 | 760371 | 0 | 35939 | 0 | 961645 | 0 | 0 | 0 | 0 | -1050985 | 2021-05-28 | 322078 | 428633 | 750711 | 0
0% | 0 | 2021-05-29 | 32897198 | 0 | 4028246 | 0 | 17879970 | 0 | 29098618 | 0 | 24226262 | 0 | 0 | 0 | 17158.558 | 0 | 0 | 10175 | 0 | 429166 | 0 | 32492 | 0 | 760371 | 0 | 35939 | 0 | 961645 | 0 | 0 | 0 | 0 | -1051724 | 2021-05-29 | 322078 | 428633 | 750711 | 0
0% | 0 | 2021-05-30 | 32897198 | 0 | 4028246 | 0 | 17879970 | 0 | 29098618 | 0 | 24226262 | 0 | 0 | 0 | 17158.558 | 0 | 0 | 10175 | 0 | 429166 | 0 | 32492 | 0 | 760371 | 0 | 35939 | 0 | 961645 | 0 | 0 | 0 | 0 | -1053131 | 2021-05-30 | 322078 | 428633 | 750711 | 0
0% | 0 | 2021-05-31 | 32897198 | 0 | 4028246 | 0 | 17879970 | 0 | 29098618 | 0 | 24226262 | 0 | 0 | 0 | 17158.558 | 0 | 0 | 10175 | 0 | 429166 | 0 | 32492 | 0 | 760371 | 0 | 35939 | 0 | 961645 | 0 | 0 | 0 | 0 | -1053131 | 2021-05-31 | 322078 | 428633 | 750711 | 0
Note on D6: amjad.abouhassan: MDB power meter ooo
Note on D7: amjad.abouhassan: MDB power meter ooo
Note on D8: amjad.abouhassan: MDB power meter ooo

## B5
[5 empty] | Boiler A |  |  |  | 71.6154 | Boiler B |  |  |  |  | Boiler C | [5 empty] | Boiler |  | SteamA |  |  |  |  | SteamB |  |  |  |  | Steam | Boiler & steam |  |  | Total Boiler Runing H | Total Steam Runing H | GAS1 % | GAS1/L | GAS2% | Gas2/L | GAS3% | GAS3/L |  | Gas Cons | Delivery | Cost/L
| Level Tank Gen | Level tank Boiler | Daily Cons Bo. | Boiler litter | Boiler A | Run Hr a | Boiler A fuel | Daily consumption | AVG | index Run H | Run Hrb | Boiler B Fuel |  | Daily consumption | Boiler C |  |  | Run C |  | Total RH | Total Fuel |  | SteamA | Run SA | Steam A Conter | Liters |  | SteamB | Run SteamB | Steam B Conter | SB Litters | Avg | Total Fuel | Total Fuel
0
2021-04-30 | 239 | 245 | 6 | 50.28 | 1825 | 1 | 12185 | 98 | 98 | 2315 | 0 | 170600 | 0 | 1869 | 2079 | 174883 | 71 | 1 | 0 | 2 | 169 |  | 2467 | 0 | 138841 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 169 | 169 | 0 | 2 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-01 | 234 | 240 | 5 | 41.9 | 1825 | 0 | 12220 | 35 | 1 | 2315 | 0 | 170650 | 50 | 1869 | 2080 | 174993 | 110 | 1 | 0 | 1 | 195 | 195 | 2467 | 0 | 138841 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 195 | 195 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-02 | 231 | 238 | 2 | 16.76 | 1825 | 0 | 12220 | 0 | 0 | 2316 | 1 | 170693 | 43 | 1869 | 2081 | 175103 | 110 | 1 | 0 | 2 | 153 | 76.5 | 2467 | 0 | 138841 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 153 | 153 | 0 | 2 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-03 | 228 | 234 | 4 | 33.52 | 1827 | 2 | 12328 | 108 | 54 | 2316 | 0 | 170693 | 0 | 1869 | 2082 | 175136 | 33 | 1 | 0 | 3 | 141 | 47 | 2467 | 0 | 138841 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 141 | 141 | 0 | 3 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-04 | 222 | 229 | 5 | 41.9 | 1827 | 0 | 12328 | 0 | 0 | 2317 | 1 | 170788 | 95 | 1869 | 2082 | 175136 | 0 | 0 | 0 | 1 | 95 | 95 | 2467 | 0 | 138841 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 95 | 95 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-05 | 216 | 222 | 7 | 58.66 | 1827 | 0 | 12328 | 0 | 0 | 2318 | 1 | 170851 | 63 | 1869 | 2083 | 175237 | 101 | 1 | 0 | 2 | 164 | 82 | 2467 | 0 | 138841 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 164 | 164 | 0 | 2 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-06 | 212 | 219 | 3 | 25.14 | 1828 | 1 | 12442 | 114 | 114 | 2318 | 0 | 170851 | 0 | 1869 | 2084 | 175278 | 41 | 1 | 0 | 2 | 155 | 77.5 | 2467 | 0 | 138841 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 155 | 155 | 0 | 2 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-07 | 205 | 212 | 7 | 58.66 | 1829 | 1 | 12491 | 49 | 49 | 2319 | 1 | 170968 | 117 | 1869 | 2084 | 175278 | 0 | 0 | 0 | 2 | 166 | 83 | 2467 | 0 | 138841 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 166 | 166 | 0 | 2 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-08 | 198 | 205 | 7 | 58.66 | 1829 | 0 | 12491 | 0 | 0 | 2320 | 1 | 171004 | 36 | 1869 | 2085 | 175398 | 120 | 1 | 0 | 2 | 156 | 78 | 2467 | 0 | 138841 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 156 | 156 | 0 | 2 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-09 | 192 | 198 | 7 | 58.66 | 1830 | 1 | 12563 | 72 | 72 | 2320 | 0 | 171004 | 0 | 1869 | 2086 | 175438 | 40 | 1 | 0 | 2 | 112 | 56 | 2467 | 0 | 138841 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 112 | 112 | 0 | 2 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-10 | 184 | 192 | 6 | 50.28 | 1830 | 0 | 12563 | 0 | 0 | 2321 | 1 | 171086 | 82 | 1869 | 2086 | 175438 | 0 | 0 | 0 | 1 | 82 | 82 | 2467 | 0 | 138841 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 82 | 82 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-11 | 234 | 241 | -49 | -410.62 | 1831 | 1 | 12644 | 81 | 81 | 2321 | 0 | 171086 | 0 | 1869 | 2086 | 175438 | 0 | 0 | 0 | 1 | 81 | 81 | 2467 | 0 | 138897 | 56 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 56 | 137 | 137 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-12 | 225 | 232 | 9 | 75.42 | 1832 | 1 | 12721 | 77 | 77 | 2321 | 0 | 171086 | 0 | 1869 | 2087 | 175515 | 77 | 1 | 0 | 2 | 154 | 77 | 2467 | 0 | 138897 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 154 | 154 | 0 | 2 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-13 | 218 | 224 | 8 | 67.04 | 1832 | 0 | 12721 | 0 | 0 | 2322 | 1 | 171201 | 115 | 1869 | 2087 | 175515 | 0 | 0 | 0 | 1 | 115 |  | 2467 | 0 | 138897 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 115 | 115 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-14 | 212 | 218 | 6 | 50.28 | 1832 | 0 | 12721 | 0 | 0 | 2322 | 0 | 171201 | 0 | 1869 | 2088 | 175604 | 89 | 1 | 0 | 1 | 89 |  | 2467 | 0 | 138897 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 89 | 89 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-15 | 206 | 213 | 5 | 41.9 | 1833 | 1 | 12810 | 89 | 89 | 2322 | 0 | 171201 | 0 | 1869 | 2089 | 175654 | 50 | 1 | 0 | 2 | 139 |  | 2467 | 0 | 138897 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 139 | 139 | 0 | 2 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-16 | 195 | 201 | 12 | 100.56 | 1833 | 0 | 12841 | 31 | 0 | 2323 | 1 | 171285 | 84 | 1869 | 2089 | 175654 | 0 | 0 | 0 | 1 | 115 |  | 2467 | 0 | 138897 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 115 | 115 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-17 | 188 | 194 | 7 | 58.66 | 1833 | 0 | 12841 | 0 | 0 | 2324 | 1 | 171322 | 37 | 1869 | 2089 | 175710 | 56 | 0 | 0 | 1 | 93 |  | 2467 | 0 | 138897 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 93 | 93 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-18 | 179 | 186 | 8 | 67.04 | 1835 | 2 | 12933 | 92 | 46 | 2324 | 0 | 171322 | 0 | 1869 | 2090 | 175754 | 44 | 1 | 0 | 3 | 136 |  | 2467 | 0 | 138897 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 136 | 136 | 0 | 3 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-19 | 170 | 178 | 8 | 67.04 | 1835 | 0 | 12933 | 0 | 0 | 2325 | 1 | 171417 | 95 | 1869 | 2090 | 175754 | 0 | 0 | 0 | 1 | 95 |  | 2467 | 0 | 138897 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 95 | 95 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-20 | 203 | 210 | -32 | -268.16 | 1835 | 0 | 12933 | 0 | 0 | 2325 | 0 | 171417 | 0 | 1869 | 2091 | 175817 | 63 | 1 | 0 | 1 | 63 |  | 2467 | 0 | 138897 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 63 | 63 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-21 | 194 | 201 | 9 | 75.42 | 1836 | 1 | 13065 | 132 | 132 | 2325 | 0 | 171439 | 22 | 1869 | 2091 | 175849 | 32 | 0 | 0 | 1 | 186 |  | 2468 | 1 | 138920 | 23 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 23 | 209 | 209 | 0 | 1 | 1 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-22 | 182 | 189 | 12 | 100.56 | 1837 | 1 | 13110 | 45 | 45 | 2326 | 1 | 171523 | 84 | 1869 | 2091 | 175849 | 0 | 0 | 0 | 2 | 129 |  | 2468 | 0 | 138920 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 129 | 129 | 0 | 2 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-23 | 176 | 182.5 | 6.5 | 54.47 | 1837 | 0 | 13110 | 0 | 0 | 2326 | 0 | 171523 | 0 | 1869 | 2092 | 175918 | 69 | 1 | 0 | 1 | 69 |  | 2468 | 0 | 138920 | 0 | 0 | 1936 | 0 | 365520.8 | 0 | 0 | 0 | 69 | 69 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-24 | 208 | 215 | -32.5 | -272.35 | 1838 | 1 | 13198 | 88 | 88 | 2326 | 0 | 171523 | 0 | 1869 | 2092 | 175918 | 0 | 0 | 0 | 1 | 88 |  | 2469 | 1 | 138993 | 73 | 0 | 1936 | 0 | 365571 | 50.2 | 0 | 123.2 | 211.2 | 211.2 | 0 | 1 | 1 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-25 | 201 | 208 | 7 | 58.66 | 1838 | 0 | 13198 | 0 | 0 | 2327 | 1 | 171613 | 90 | 1869 | 2092 | 175918 | 0 | 0 | 0 | 1 | 90 |  | 2469 | 0 | 138993 | 0 | 0 | 1936 | 0 | 365571 | 0 | 0 | 0 | 90 | 90 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-26 | 187 | 194 | 14 | 117.32 | 1838 | 0 | 13198 | 0 | 0 | 2327 | 0 | 171613 | 0 | 1869 | 2093 | 176032 | 114 | 1 | 0 | 1 | 114 |  | 2469 | 0 | 138993 | 0 | 0 | 1936 | 0 | 365571 | 0 | 0 | 0 | 114 | 114 | 0 | 1 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-27 | 177 | 184 | 10 | 83.8 | 1839 | 1 | 13281 | 83 | 83 | 2327 | 0 | 171613 | 0 | 1869 | 2094 | 176055 | 23 | 1 | 0 | 2 | 106 |  | 2469 | 0 | 138993 | 0 | 0 | 1936 | 0 | 365571 | 0 | 0 | 0 | 106 | 106 | 0 | 2 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-28 | 177 | 184 | 0 | 0 | 1839 | 0 | 13281 | 0 | 0 | 2327 | 0 | 171613 | 0 | 1869 | 2094 | 176055 | 0 | 0 | 0 | 0 | 0 |  | 2469 | 0 | 138993 | 0 | 0 | 1936 | 0 | 365571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-29 | 177 | 184 | 0 | 0 | 1839 | 0 | 13281 | 0 | 0 | 2327 | 0 | 171613 | 0 | 1869 | 2094 | 176055 | 0 | 0 | 0 | 0 | 0 |  | 2469 | 0 | 138993 | 0 | 0 | 1936 | 0 | 365571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-30 | 177 | 184 | 0 | 0 | 1839 | 0 | 13281 | 0 | 0 | 2327 | 0 | 171613 | 0 | 1869 | 2094 | 176055 | 0 | 0 | 0 | 0 | 0 |  | 2469 | 0 | 138993 | 0 | 0 | 1936 | 0 | 365571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
2021-05-31 | 177 | 184 | 0 | 0 | 1839 | 0 | 13281 | 0 | 0 | 2327 | 0 | 171613 | 0 | 1869 | 2094 | 176055 | 0 | 0 | 0 | 0 | 0 |  | 2469 | 0 | 138993 | 0 | 0 | 1936 | 0 | 365571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 2010 | 55 | 1650 | 61 | 1830 | 5490 | 0 |  |  | 0.8
[9 empty] | 71.6154 | [11 empty] | 3281 | [8 empty] | . |  |  | 202.2 |  |  |  | 41 | 2 |  |  |  |  | Nb Delivery | 0 |  | 0 | 0 | #DIV/0!
[33 empty] | 0 | 3483.2
[33 empty] | 0 | [12 empty] | 0 | 0 | #DIV/0!
0

## WATER
|  |  | 8057178 | [38 empty] | Entrance |  | Tank 1 |  | Tank 2
[42 empty] | Level |  |  |  |  | Quantity CM3 |  |  | Var
Date | Truck | Truck M3/day | N0. Trucks |  | REQ. # of trucks | City | City/day | Total water delivery |  | SW | Cosum SW/day | RO Guest/ Liter |  | RO K&L/ Liter |  | TOTAL RO Production | RO 1 RH | RO 2 RH | RO water counter | RO Cons m3 | Steam Boiler | Steam Boiler/day | Softener Guest | Guest Sotf/day | Softener K&L | K&L Soft/Day | Fire Tank Level | Fire Tank Counter |  | Laundry Hot Water Counter | Hot Water Cons/day | Laundry Cold Water Counter | Cold Water Cons/day | Laundry Water Total Cons | K&L Sotf/day | Guest / day | K&L /day | Avg Outside Temp | Banquet Activity |  |  | Date |  | MainI |  | Kitchen and Laundry |  | Guest | Main Tank | Kitchen and Laundry | Guest | Kitchen and Laundry | Main | Guest | Total VAR | Hotel Consumption
|  |  |  | 1.66 | [34 empty] | Ball R | Meeting | outlet |  |  | 180 |  | 220 |  | 580 | 180 | 220 | 580
2021-05-30 | 109443 | 0 | 0 | 250 |  | 618491 | 0 | 0 | 0 | 6751 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 470 | 0 | 151413 | 0 | 98768 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 23 | 0 |  | 0 | 44346 | 0.9 | 80 | 1.1 | 150 | 2.9 | 141 | 72 | 165 | 408.9 | -9 | -2.2 | -11.6 | -22.8 | 22.8 | -22.8
2021-05-01 | 109443 | 0 | 0 | 241.9355 |  | 618498 | 7 | 7 | 34.5622 | 6751 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 470 | 0 | 151413 | 0 | 98768 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 23.5 | 0 |  | 0 | 2021-05-01 | 0.9 | 81 | 1.1 | 148 | 2.9 | 139 | 72.9 | 162.8 | 403.1 | 0.9 | -2.2 | -5.8 | -7.1 | 14.1 | -7.1
2021-05-02 | 109443 | 0 | 0 | 241.9355 |  | 618498 | 0 | 0 | 0 | 6754 | 3 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 470 | 0 | 151413 | 0 | 98768 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | -3 | 0 | 23 | 0 |  | 0 | 2021-05-02 | 0.9 | 82 | 1.1 | 146 | 2.9 | 138 | 73.8 | 160.6 | 400.2 | 0.9 | -2.2 | -2.9 | -4.2 | 4.2 | -4.2
2021-05-03 | 109443 | 0 | 0 | 241.9355 |  | 618787 | 289 | 289 | 0.83715 | 6754 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 470 | 0 | 151495 | 82 | 98804 | 36 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 36 | 82 | 36 | 24 | 0 |  | 0 | 2021-05-03 | 0.9 | 99 | 1.1 | 170 | 2.9 | 158 | 89.1 | 187 | 458.2 | 15.3 | 26.4 | 58 | 99.7 | 189.3 | 99.7
2021-05-04 | 109443 | 0 | 0 | 241.9355 |  | 618787 | 0 | 0 | 0 | 6754 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 1 | 151496 | 1 | 98804 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 1 | -1 | 22.5 | 0 |  | 0 | 2021-05-04 | 0.9 | 82 | 1.1 | 169 | 2.9 | 154 | 73.8 | 185.9 | 446.6 | -15.3 | -1.1 | -11.6 | -28 | 28 | -28
2021-05-05 | 109443 | 0 | 0 | 241.9355 |  | 619082 | 295 | 295 | 0.82012 | 6754 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151601 | 105 | 98804 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 105 | 0 | 23 | 0 |  | 0 | 2021-05-05 | 0.9 | 104 | 1.1 | 167 | 2.9 | 177 | 93.6 | 183.7 | 513.3 | 19.8 | -2.2 | 66.7 | 84.3 | 210.7 | 84.3
2021-05-06 | 109443 | 0 | 0 | 241.9355 |  | 619082 | 0 | 0 | 0 | 6760 | 6 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151601 | 0 | 98804 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | -6 | 0 | 22 | 0 |  | 0 | 2021-05-06 | 0.9 | 104 | 1.1 | 165 | 2.9 | 176 | 93.6 | 181.5 | 510.4 | 0 | -2.2 | -2.9 | -5.1 | 5.1 | -5.1
2021-05-07 | 109443 | 0 | 0 | 241.9355 |  | 619375 | 293 | 293 | 0.82572 | 6760 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151746 | 145 | 98804 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 145 | 0 | 23 | 0 |  | 0 | 2021-05-07 | 0.9 | 86 | 1.1 | 163 | 2.9 | 201 | 77.4 | 179.3 | 582.9 | -16.2 | -2.2 | 72.5 | 54.1 | 238.9 | 54.1
2021-05-08 | 109443 | 0 | 0 | 241.9355 |  | 619375 | 0 | 0 | 0 | 6760 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151746 | 0 | 98836 | 32 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 32 | 0 | 32 | 24.5 | 0 |  | 0 | 2021-05-08 | 0.9 | 58 | 1.1 | 182 | 2.9 | 190 | 52.2 | 200.2 | 551 | -25.2 | 20.9 | -31.9 | -36.2 | 36.2 | -36.2
2021-05-09 | 109443 | 0 | 0 | 241.9355 |  | 619375 | 0 | 0 | 0 | 6762 | 2 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151772 | 26 | 98847 | 11 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 11 | 24 | 11 | 24.5 | 0 |  | 0 | 2021-05-09 | 0.9 | 164 | 1.1 | 189 | 2.9 | 187 | 147.6 | 207.9 | 542.3 | 95.4 | 7.7 | -8.7 | 94.4 | -94.4 | 94.4
2021-05-10 | 109443 | 0 | 0 | 241.9355 |  | 619375 | 0 | 0 | 0 | 6762 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151772 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 22 | 0 |  | 0 | 2021-05-10 | 0.9 | 169 | 1.1 | 188 | 2.9 | 181 | 152.1 | 206.8 | 524.9 | 4.5 | -1.1 | -17.4 | -14 | 14 | -14
2021-05-11 | 109443 | 0 | 0 | 241.9355 |  | 619375 | 0 | 0 | 0 | 6762 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151772 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 21 | 0 |  | 0 | 2021-05-11 | 0.9 | 133 | 1.1 | 185 | 2.9 | 177 | 119.7 | 203.5 | 513.3 | -32.4 | -3.3 | -11.6 | -47.3 | 47.3 | -47.3
2021-05-12 | 109443 | 0 | 0 | 241.9355 |  | 619375 | 0 | 0 | 0 | 6762 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151772 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 22 | 0 |  | 0 | 2021-05-12 | 0.9 | 133 | 1.1 | 184 | 2.9 | 172 | 119.7 | 202.4 | 498.8 | 0 | -1.1 | -14.5 | -15.6 | 15.6 | -15.6
2021-05-13 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 341 | 341 | 0.70949 | 6762 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151772 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 21 | 0 |  | 0 | 2021-05-13 | 0.9 | 133 | 1.1 | 184 | 2.9 | 161 | 119.7 | 202.4 | 466.9 | 0 | 0 | -31.9 | -31.9 | 372.9 | -31.9
2021-05-14 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6762 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151772 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 22.5 | 0 |  | 0 | 2021-05-14 | 0.9 | 133 | 1.1 | 183 | 2.9 | 161 | 119.7 | 201.3 | 466.9 | 0 | -1.1 | 0 | -1.1 | 1.1 | -1.1
2021-05-15 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6762 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151772 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 23.5 | 0 |  | 0 | 2021-05-15 | 0.9 | 133 | 1.1 | 182 | 2.9 | 153 | 119.7 | 200.2 | 443.7 | 0 | -1.1 | -23.2 | -24.3 | 24.3 | -24.3
2021-05-16 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6766 | 4 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151772 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | -4 | 0 | 21.5 | 0 |  | 0 | 2021-05-16 | 0.9 | 133 | 1.1 | 181 | 2.9 | 144 | 119.7 | 199.1 | 417.6 | 0 | -1.1 | -26.1 | -27.2 | 27.2 | -27.2
2021-05-17 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6766 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151772 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 22.5 | 0 |  | 0 | 2021-05-17 | 0.9 | 133 | 1.1 | 181 | 2.9 | 136 | 119.7 | 199.1 | 394.4 | 0 | 0 | -23.2 | -23.2 | 23.2 | -23.2
2021-05-18 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6768 | 2 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 471 | 0 | 151772 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | -2 | 0 | 23 | 0 |  | 0 | 2021-05-18 | 0.9 | 130 | 1.1 | 180 | 2.9 | 126 | 117 | 198 | 365.4 | -2.7 | -1.1 | -29 | -32.8 | 32.8 | -32.8
2021-05-19 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6769 | 1 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 472 | 1 | 151832 | 60 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 59 | -1 | 23 | 0 |  | 0 | 2021-05-19 | 0.9 | 64 | 1.1 | 180 | 2.9 | 117 | 57.6 | 198 | 339.3 | -59.4 | 0 | -26.1 | -85.5 | 85.5 | -85.5
2021-05-20 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6769 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 472 | 0 | 151832 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 23.5 | 0 |  | 0 | 2021-05-20 | 0.9 | 64 | 1.1 | 179 | 2.9 | 111 | 57.6 | 196.9 | 321.9 | 0 | -1.1 | -17.4 | -18.5 | 18.5 | -18.5
2021-05-21 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6769 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 472 | 0 | 151832 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 24.5 | 0 |  | 0 | 2021-05-21 | 0.9 | 64 | 1.1 | 178 | 2.9 | 108 | 108 | 195.8 | 313.2 | 50.4 | -1.1 | -8.7 | 40.6 | -40.6 | 40.6
2021-05-22 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6770 | 1 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 472 | 0 | 151832 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | -1 | 0 | 24.5 | 0 |  | 0 | 2021-05-22 | 0.9 | 120 | 1.1 | 177 | 2.9 | 105 | 108 | 194.7 | 304.5 | 0 | -1.1 | -8.7 | -9.8 | 9.8 | -9.8
2021-05-23 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6770 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 472 | 0 | 151832 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 23.5 | 0 |  | 0 | 2021-05-23 | 0.9 | 120 | 1.1 | 176 | 2.9 | 102 | 108 | 193.6 | 295.8 | 0 | -1.1 | -8.7 | -9.8 | 9.8 | -9.8
2021-05-24 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6770 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 472 | 0 | 151832 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 24.5 | 0 |  | 0 | 2021-05-24 | 0.9 | 120 | 1.1 | 175 | 2.9 | 115 | 108 | 192.5 | 333.5 | 0 | -1.1 | 37.7 | 36.6 | -36.6 | 36.6
2021-05-25 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6770 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 472 | 0 | 151832 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.78 | 0 | 2205.62 | 0 | 0 | 0 | 0 | 0 | 24.5 | 0 |  | 0 | 2021-05-25 | 0.9 | 84 | 1.1 | 172 | 2.9 | 111 | 75.6 | 189.2 | 321.9 | -32.4 | -3.3 | -11.6 | -47.3 | 47.3 | -47.3
2021-05-26 | 109443 | 0 | 0 | 241.9355 |  | 619716 | 0 | 0 | 0 | 6773 | 3 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 474 | 2 | 151834 | 2 | 98847 | 0 | 261 | 731 | 0 | 229.81 | 0.03 | 2205.98 | 0.36 | 0.39 | 0 | -1 | -2 | 24.5 | 0 |  | 0 | 2021-05-26 | 0.9 | 65 | 1.1 | 169 | 2.9 | 105 | 58.5 | 185.9 | 304.5 | -17.1 | -3.3 | -17.4 | -37.8 | 37.8 | -37.8
2021-05-27 | 109443 | 0 | 0 | 241.9355 |  | 620151 | 435 | 435 | 0.55617 | 6773 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 474 | 0 | 151905 | 71 | 98847 | 0 | 261 | 731 | 0 | 229.81 | 0 | 2205.98 | 0 | 0 | 0 | 71 | 0 | 23.5 | 0 |  | 0 | 2021-05-27 | 0.9 | 120 | 1.1 | 168 | 2.9 | 117 | 108 | 184.8 | 339.3 | 49.5 | -1.1 | 34.8 | 83.2 | 351.8 | 83.2
2021-05-28 | 109443 | 0 | 0 | 241.9355 |  | 620151 | 0 | 0 | 0 | 6773 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 474 | 0 | 151905 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.81 | 0 | 2205.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2021-05-28 | 0.9 | 120 | 1.1 | 168 | 2.9 | 117 | 108 | 184.8 | 339.3 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-29 | 109443 | 0 | 0 | 241.9355 |  | 620151 | 0 | 0 | 0 | 6773 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 474 | 0 | 151905 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.81 | 0 | 2205.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2021-05-29 | 0.9 | 120 | 1.1 | 168 | 2.9 | 117 | 108 | 184.8 | 339.3 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-30 | 109443 | 0 | 0 | 241.9355 |  | 620151 | 0 | 0 | 0 | 6773 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 474 | 0 | 151905 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.81 | 0 | 2205.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2021-05-30 | 0.9 | 120 | 1.1 | 168 | 2.9 | 117 | 108 | 184.8 | 339.3 | 0 | 0 | 0 | 0 | 0 | 0
2021-05-31 | 109443 | 0 | 0 | 241.9355 |  | 620151 | 0 | 0 | 0 | 6773 | 0 | 457.44 | 0 | 529.52 | 0 | 0 |  |  | 5171 | 0 | 474 | 0 | 151905 | 0 | 98847 | 0 | 261 | 731 | 0 | 229.81 | 0 | 2205.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  | 0 | 0 |  | 0 |  | 1660 | 1660 |  |  | 22 |  |  |  |  | 0 |  |  |  | 0 |  |  |  | 3 | [10 empty] | 79 | -19 | 75
|  | 0 |  | 6774.1935 | 0 |  | 7500 | 0 | [5 empty] | 1660 | [10 empty] | 82 | [10 empty] | 0
| 243 |  | 0 |  | 0 | 1660 | 7500 |  |  | 4.5181 | [24 empty] | 0 |  |  | #DIV/0!
Formulas:
Level = [Date]

## GEN
| GEN1 | RUN HR | Fuel Counter Index | Cons /day | Diesel L/H |  | next service | ALARM | GEN2 | RUN HR | Fuel Counter Index | Cons /day | Diesel L/H |  | next service | ALARM | GEN3 | RUN HR | Fuel Counter Index | Cons /day | Diesel L/H |  | next service | ALARM | RH total | Gen Con /day | Total Deisel Cons/day | H /L | TOAL KW GEN |  |  |  |  | fuel Consuption |  | AVG KW/h
2021-04-30 | 9893 | 8 | 386061 | 1483.7 | 185.4625 |  | 9934 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12150 | 0 | 438163 | 0 | 250 |  | 12192 | ok | 8 | 1483.7 | 435.4625 | 185.4625 | 0 | 0 | 0 | 0 | 185.4625 | 0 | 0.25738 | 0
2021-05-01 | 9899 | 6 | 387090 | 1029 | 171.5 | 0 | 9934 | ok | 10698 | 0 | 357691 | 0 | 0 | 0 | 10873 | ok | 12150 | 0 | 438163 | 0 | 250 | 0 | 12192 | ok | 6 | 1029 | 421.5 | 171.5 | 3927 | 654.5 | 40.91% | 147.2625 | 24.2375 | 1010.7468 | 0.25738 | 168.4578
2021-05-02 | 9902 | 3 | 387585 | 495 | 165 |  | 9934 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12150 | 0 | 438163 | 0 | 250 |  | 12192 | ok | 3 | 495 | 415 | 165 | 1996 | 665.3333 | 41.58% | 149.7 | 15.3 | 513.7384 | 0.25738 | 171.2461
2021-05-03 | 9906 | 4 | 388259 | 674 | 168.5 |  | 9934 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12150 | 0 | 438163 | 0 | 250 |  | 12192 | ok | 4 | 674 | 418.5 | 168.5 | 3020 | 755 | 47.19% | 151 | 17.5 | 777.2996 | 0.25738 | 194.3249
2021-05-04 | 9914 | 8 | 389826 | 1567 | 195.875 |  | 9934 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12150 | 0 | 438163 | 0 | 250 |  | 12192 | ok | 8 | 1567 | 445.875 | 195.875 | 4211 | 526.375 | 32.9% | 105.275 | 90.6 | 1083.8439 | 0.25738 | 135.4805
2021-05-05 | 9923 | 9 | 391322.9 | 1496.9 | 166.3222 |  | 9934 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12150 | 0 | 438163 | 0 | 250 |  | 12192 | ok | 9 | 1496.9 | 416.3222 | 166.3222 | 5610 | 623.3333 | 38.96% |  | #VALUE! | 1443.9241 | 0.25738 | 160.436
2021-05-06 | 9929 | 6 | 392266.5 | 943.6 | 157.2667 |  | 9934 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12150 | 0 | 438163 | 0 | 250 |  | 12192 | ok | 6 | 943.6 | 407.2667 | 157.2667 | 3482 | 580.3333 | 36.27% | 116.0667 | 41.2 | 896.211 | 0.25738 | 149.3685
2021-05-07 | 9937.5 | 8.5 | 394000.4 | 1733.9 | 203.9882 |  | 9934 | oil change | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12150 | 0 | 438163 | 0 | 250 |  | 12192 | ok | 8.5 | 1733.9 | 453.9882 | 203.9882 | 5855 | 688.8235 | 43.05% | 137.7647 | 66.2235 | 1506.9831 | 0.25738 | 177.2921
2021-05-08 | 9946.1 | 8.6 | 394894 | 893.6 | 103.907 |  | 9934 | oil change | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12150 | 0 | 438163 | 0 | 250 |  | 12192 | ok | 8.6 | 893.6 | 353.907 | 103.907 | 5509 | 640.5814 | 40.04% | 128.1163 | -24.2093 | 1417.9283 | 0.25738 | 164.8754
2021-05-09 | 9955 | 8.9 | 396250 | 1356 | 152.3596 |  | 9934 | oil change | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12150 | 0 | 438163 | 0 | 250 |  | 12192 | ok | 8.9 | 1356 | 402.3596 | 152.3596 | 6303 | 708.2022 | 44.26% | 141.6404 | 10.7191 | 1622.2911 | 0.25738 | 182.2799
2021-05-10 | 9955 | 0 | 396268 | 18 | 0 |  | 9934 | oil change | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12159 | 9 | 440413 | 2250 | 250 |  | 12192 | ok | 9 | 2268 | 250 | 252 | 6338 | 704.2222 | 44.01% | 140.8444 | 111.1556 | 1631.2996 | 0.25738 | 181.2555
2021-05-11 | 9955 | 0 | 396271 | 3 | 0 |  | 9934 | oil change | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12169 | 10 | 440413 | 2500 | 250 |  | 12192 | ok | 10 | 2503 | 250 | 250.3 | 5744 | 574.4 | 35.9% | 114.88 | 135.42 | 1478.4135 | 0.25738 | 147.8414
2021-05-12 | 9964 | 9 | 397879 | 1608 | 178.6667 |  | 9934 | oil change | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12172 | 3 | 3669836 | 750 | 250 |  | 12192 | ok | 12 | 2358 | 428.6667 | 196.5 | 7269 | 605.75 | 37.86% | 121.15 | 75.35 | 1870.9241 | 0.25738 | 155.9103
2021-05-13 | 9973 | 9 | 398972 | 1093 | 121.4444 |  | 9934 | oil change | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12172 | 0 | 3669836 | 0 | 250 |  | 12192 | ok | 9 | 1093 | 371.4444 | 121.4444 | 6705 | 745 | 46.56% | 149 | -27.5556 | 1725.7595 | 0.25738 | 191.7511
2021-05-14 | 9983 | 10 | 400946 | 1974 | 197.4 |  | 9934 | oil change | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12172 | 0 | 3669836 | 0 | 250 |  | 12192 | ok | 10 | 1974 | 447.4 | 197.4 | 5385 | 538.5 | 33.66% | 107.7 | 89.7 | 1386.0127 | 0.25738 | 138.6013
2021-05-15 | 9990 | 7 | 402914 | 1968 | 281.1429 |  | 9934 | oil change | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12172 | 0 | 3669836 | 0 | 250 |  | 12192 | ok | 7 | 1968 | 531.1429 | 281.1429 | 6396 | 913.7143 | 57.11% | 182.7429 | 98.4 | 1646.2278 | 0.25738 | 235.1754
2021-05-16 | 10006 | 16 | 404363.8 | 1449.8 | 90.6125 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12172 | 0 | 3669836 | 0 | 250 |  | 12192 | ok | 16 | 1449.8 | 340.6125 | 90.6125 | 5025 | 314.0625 | 19.63% | 62.8125 | 27.8 | 1293.3544 | 0.25738 | 80.8347
2021-05-17 | 10015 | 9 | 405397 | 1033.2 | 114.8 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12172 | 0 | 3669836 | 0 | 250 |  | 12192 | ok | 9 | 1033.2 | 364.8 | 114.8 | 9392 | 1043.5556 | 65.22% | 208.7111 | -93.9111 | 2417.3502 | 0.25738 | 268.5945
2021-05-18 | 10026 | 11 | 406672 | 1275 | 115.9091 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12172 | 0 | 3669836 | 0 | 250 |  | 12192 | ok | 11 | 1275 | 365.9091 | 115.9091 | 8787 | 798.8182 | 49.93% | 159.7636 | -43.8545 | 2261.6329 | 0.25738 | 205.603
2021-05-19 | 10042 | 16 | 408288 | 1616 | 101 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12172 | 0 | 3669836 | 0 | 250 |  | 12192 | ok | 16 | 1616 | 351 | 101 | 12246 | 765.375 | 47.84% | 153.075 | -52.075 | 3151.9241 | 0.25738 | 196.9953
2021-05-20 | 10052 | 10 | 409524 | 1500 | 150 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12172 | 0 | 3669836 | 0 | 250 |  | 12192 | ok | 10 | 1500 | 400 | 150 | 7337 | 733.7 | 45.86% | 146.74 | 3.26 | 1888.4262 | 0.25738 | 188.8426
2021-05-21 | 10054 | 2 | 409912 | 300 | 150 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12182 | 10 | 369837 | 2500 | 250 |  | 12192 | ok | 12 | 2800 | 400 | 233.3333 | 7952 | 662.6667 | 41.42% | 132.5333 | 100.8 | 2046.7173 | 0.25738 | 170.5598
2021-05-22 | 10054 | 0 | 409912 | 0 | 0 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12198 | 16 | 373837 | 4000 | 250 |  | 12192 | oil change | 16 | 4000 | 250 | 250 | 10547 | 659.1875 | 41.2% | 131.8375 | 118.1625 | 2714.6287 | 0.25738 | 169.6643
2021-05-23 | 10054 | 0 | 409912 | 0 | 0 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12206 | 8 | 375837 | 2000 | 250 |  | 12192 | oil change | 8 | 2000 | 250 | 250 | 5535 | 691.875 | 43.24% | 138.375 | 111.625 | 1424.6203 | 0.25738 | 178.0775
2021-05-24 | 10054 | 0 | 409912 | 0 | 0 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12223 | 17 | 380087 | 4250 | 250 |  | 12192 | oil change | 17 | 4250 | 250 | 250 | 12454 | 732.5882 | 45.79% | 146.5176 | 103.4824 | 3205.4599 | 0.25738 | 188.5565
2021-05-25 | 10054 | 0 | 409912 | 0 | 0 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12232 | 9 | 380087 | 2250 | 250 |  | 12342 | ok | 9 | 2250 | 250 | 250 | 6175 | 686.1111 | 42.88% | 137.2222 | 112.7778 | 1589.346 | 0.25738 | 176.594
2021-05-26 | 10064 | 10 | 411327 | 1415 | 141.5 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12240 | 8 | 382087 | 2000 | 250 |  | 12342 | ok | 18 | 3415 | 391.5 | 189.7222 | 13086 | 727 | 45.44% | 145.4 | 44.3222 | 3368.1266 | 0.25738 | 187.1181
2021-05-27 | 10077 | 13 | 412973 | 1646 | 126.6154 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12240 | 0 | 382087 | 0 | 250 |  | 12342 | ok | 13 | 1646 | 376.6154 | 126.6154 | 9436 | 725.8462 | 45.37% | 145.1692 | -18.5538 | 2428.6751 | 0.25738 | 186.8212
2021-05-28 | 10077 | 0 | 412973 | 0 | 0 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12240 | 0 | 382087 | 0 | 250 |  | 12342 | ok | 0 | 0 | 250 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0.25738 | 0
2021-05-29 | 10077 | 0 | 412973 | 0 | 0 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12240 | 0 | 382087 | 0 | 250 |  | 12342 | ok | 0 | 0 | 250 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0.25738 | 0
2021-05-30 | 10077 | 0 | 412973 | 0 | 0 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12240 | 0 | 382087 | 0 | 250 |  | 12342 | ok | 0 | 0 | 250 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0.25738 | 0
2021-05-31 | 10077 | 0 | 412973 | 0 | 0 |  | 10105 | ok | 10698 | 0 | 357691 | 0 | 0 |  | 10873 | ok | 12240 | 0 | 382087 | 0 | 250 |  | 12342 | ok | 0 | 0 | 250 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0.25738 | 0
[15 empty] | 0 |  |  |  |  | 274 |  |  | 341 |  | 274
|  | 184 | [7 empty] | 0 | [7 empty] | 90
Note on C27: amjad.abouhassan: Added manually counter OOO

## tanks
| Tank 1 |  | Tank 2 |  | Tank 3 |  | Tank 4 |  | Tank 5 |  | Tank 6 |  | Tank 7 |  | Tank 8 |  | Tank 9 |  | Tank 10 |  | Tank 11 |  |  |  | Tank 1 |  | Tank 2 |  | Tank 3 |  | Tank 4 |  | Tank 5 |  | Tank 6 |  | Tank 7
| 6670 |  | 6670 |  | 6670 |  | 6670 |  | 6670 |  | 6670 |  | 6670 |  | 6670 |  | 6670 |  | 6670 |  | 6670 | 73370 |  |  | 2800 |  | 2800 |  | 2800 |  | 2800 |  | 2800 |  | 2800 |  | 2800 | 19600 |  | 92970 |  | Total sotck | Diesel Cons Per day | Diesel Delivery | [10 empty] | Genset Co | Steam | Boil | Outdoor temperature
| 21.5161 |  | 21.5161 |  | 21.5161 |  | 21.5161 |  | 21.5161 |  | 21.5161 |  | 21.5161 |  | 21.5161 |  | 21.5161 |  | 21.5161 |  | 21.5161 |  |  |  | 10 | 0 | 10 | 0 | 10 | 0 | 10 | 0 | 10 | 0 | 10 | 0 | 10 | [6 empty] | Delivery | Cost /L |  | Boiler+Steam | Generator |  | Occupancy | AVE TEPM | AVE Humidity
2021-04-30 | 239 | 5142.3548 | 239 | 5142.3548 | 239 | 5142.3548 | 239 | 5142.3548 | 239 | 5142.3548 | 239 | 5142.3548 | 239 | 5142.3548 | 239 | 5142.3548 | 239 | 5142.3548 | 239 | 5142.3548 | 239 | 5142.3548 | 77.1% | 56565.9032 | 245 | 2450 | 245 | 2450 | 245 | 2450 | 245 | 2450 | 245 | 2450 | 245 | 2450 | 245 | 2450 | 87.5% | 17150 | 79.29% | 73715.9032 | 0 |  |  | 0.92 | -169 | -1434.3871 | -1603.3871 | 0% | 23 | 56% | 0 | 19222 | #REF! | 0 | #REF! | 0
2021-05-01 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 75.48% | 55382.5161 | 240 | 2400 | 240 | 2400 | 240 | 2400 | 240 | 2400 | 240 | 2400 | 240 | 2400 | 240 | 2400 | 85.71% | 16800 | 77.64% | 72182.5161 | -1533.3871 |  |  | 0.92 | -195 | -1338.3871 | -1533.3871 | 0% | 23.5 | 65% | 0 | 19222 | 513.7384 |  | #REF! | 21 | 12 | -111.5323 | 40.91%
2021-05-02 | 231 | 4970.2258 | 231 | 4970.2258 | 231 | 4970.2258 | 231 | 4970.2258 | 231 | 4970.2258 | 231 | 4970.2258 | 231 | 4970.2258 | 231 | 4970.2258 | 231 | 4970.2258 | 231 | 4970.2258 | 231 | 4970.2258 | 74.52% | 54672.4839 | 238 | 2380 | 238 | 2380 | 238 | 2380 | 238 | 2380 | 238 | 2380 | 238 | 2380 | 238 | 2380 | 85% | 16660 | 76.73% | 71332.4839 | -850.0323 |  |  | 0.92 | -153 | -697.0323 | -850.0323 | 0% | 23 | 67% | 0 | 19222 | 777.2996 |  | #REF! | 19 | 15 | -46.4688 | 41.58%
2021-05-03 | 228 | 4905.6774 | 228 | 4905.6774 | 228 | 4905.6774 | 228 | 4905.6774 | 228 | 4905.6774 | 228 | 4905.6774 | 228 | 4905.6774 | 228 | 4905.6774 | 228 | 4905.6774 | 228 | 4905.6774 | 228 | 4905.6774 | 73.55% | 53962.4516 | 234 | 2340 | 234 | 2340 | 234 | 2340 | 234 | 2340 | 234 | 2340 | 234 | 2340 | 234 | 2340 | 83.57% | 16380 | 75.66% | 70342.4516 | -990.0323 |  |  | 0.92 | -141 | -849.0323 | -990.0323 | 0% | 24 | 65% | 0 | 19222 | 1083.8439 |  | #REF! | 16 | 9 | -94.3369 | 47.19%
2021-05-04 | 222 | 4776.5806 | 222 | 4776.5806 | 222 | 4776.5806 | 222 | 4776.5806 | 222 | 4776.5806 | 222 | 4776.5806 | 222 | 4776.5806 | 222 | 4776.5806 | 222 | 4776.5806 | 222 | 4776.5806 | 222 | 4776.5806 | 71.61% | 52542.3871 | 229 | 2290 | 229 | 2290 | 229 | 2290 | 229 | 2290 | 229 | 2290 | 229 | 2290 | 229 | 2290 | 81.79% | 16030 | 73.76% | 68572.3871 | -1770.0645 |  |  | 0.92 | -95 | -1675.0645 | -1770.0645 | 0% | 22.5 | 44% | 0 | 19222 | 1443.9241 |  | #REF! | 18 | 6 | -279.1774 | 32.9%
2021-05-05 | 216 | 4647.4839 | 216 | 4647.4839 | 216 | 4647.4839 | 216 | 4647.4839 | 216 | 4647.4839 | 216 | 4647.4839 | 216 | 4647.4839 | 216 | 4647.4839 | 216 | 4647.4839 | 216 | 4647.4839 | 216 | 4647.4839 | 69.68% | 51122.3226 | 222 | 2220 | 222 | 2220 | 222 | 2220 | 222 | 2220 | 222 | 2220 | 222 | 2220 | 222 | 2220 | 79.29% | 15540 | 71.7% | 66662.3226 | -1910.0645 |  |  | 0.92 | -164 | -1746.0645 | -1910.0645 | 0% | 23 | 53% | 0 | 19222 | 896.211 |  | #REF! | 16 | 7 | -249.4378 | 38.96%
2021-05-06 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 68.39% | 50175.6129 | 219 | 2190 | 219 | 2190 | 219 | 2190 | 219 | 2190 | 219 | 2190 | 219 | 2190 | 219 | 2190 | 78.21% | 15330 | 70.46% | 65505.6129 | -1156.7097 |  |  | 0.92 | -155 | -1001.7097 | -1156.7097 | 0% | 22 | 64% | 0 | 19222 | 1506.9831 |  | #REF! | 16.5 | 9.3 | -107.7107 | 36.27%
2021-05-07 | 205 | 4410.8065 | 205 | 4410.8065 | 205 | 4410.8065 | 205 | 4410.8065 | 205 | 4410.8065 | 205 | 4410.8065 | 205 | 4410.8065 | 205 | 4410.8065 | 205 | 4410.8065 | 205 | 4410.8065 | 205 | 4410.8065 | 66.13% | 48518.871 | 212 | 2120 | 212 | 2120 | 212 | 2120 | 212 | 2120 | 212 | 2120 | 212 | 2120 | 212 | 2120 | 75.71% | 14840 | 68.15% | 63358.871 | -2146.7419 |  |  | 0.92 | -166 | -1980.7419 | -2146.7419 | 0% | 23 | 65% | 0 | 19222 | 1417.9283 |  | #REF! | 15.5 | 3.7 | -535.3357 | 43.05%
2021-05-08 | 198 | 4260.1935 | 198 | 4260.1935 | 198 | 4260.1935 | 198 | 4260.1935 | 198 | 4260.1935 | 198 | 4260.1935 | 198 | 4260.1935 | 198 | 4260.1935 | 198 | 4260.1935 | 198 | 4260.1935 | 198 | 4260.1935 | 63.87% | 46862.129 | 205 | 2050 | 205 | 2050 | 205 | 2050 | 205 | 2050 | 205 | 2050 | 205 | 2050 | 205 | 2050 | 73.21% | 14350 | 65.84% | 61212.129 | -2146.7419 |  |  | 0.92 | -156 | -1990.7419 | -2146.7419 | 0% | 24.5 | 52% | 0 | 19222 | 1622.2911 |  | #REF! |  | 5 | -398.1484 | 40.04%
2021-05-09 | 192 | 4131.0968 | 192 | 4131.0968 | 192 | 4131.0968 | 192 | 4131.0968 | 192 | 4131.0968 | 192 | 4131.0968 | 192 | 4131.0968 | 192 | 4131.0968 | 192 | 4131.0968 | 192 | 4131.0968 | 192 | 4131.0968 | 61.94% | 45442.0645 | 198 | 1980 | 198 | 1980 | 198 | 1980 | 198 | 1980 | 198 | 1980 | 198 | 1980 | 198 | 1980 | 70.71% | 13860 | 63.79% | 59302.0645 | -1910.0645 |  |  | 0.92 | -112 | -1798.0645 | -1910.0645 | 0% | 24.5 | 55% | 0 | 19222 | 1631.2996 |  | #REF! |  | 3 | -599.3548 | 44.26%
2021-05-10 | 184 | 3958.9677 | 184 | 3958.9677 | 184 | 3958.9677 | 184 | 3958.9677 | 184 | 3958.9677 | 184 | 3958.9677 | 184 | 3958.9677 | 184 | 3958.9677 | 184 | 3958.9677 | 184 | 3958.9677 | 184 | 3958.9677 | 59.35% | 43548.6452 | 192 | 1920 | 192 | 1920 | 192 | 1920 | 192 | 1920 | 192 | 1920 | 192 | 1920 | 192 | 1920 | 68.57% | 13440 | 61.3% | 56988.6452 | -2313.4194 |  |  | 0.92 | -82 | -2231.4194 | -2313.4194 | 0% | 22 | 53% | 0 | 19222 | 1478.4135 |  | #REF! |  | 4 | -557.8548 | 44.01%
2021-05-11 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 234 | 5034.7742 | 75.48% | 55382.5161 | 241 | 2410 | 241 | 2410 | 241 | 2410 | 241 | 2410 | 241 | 2410 | 241 | 2410 | 241 | 2410 | 86.07% | 16870 | 77.72% | 72252.5161 | 718.871 | 14545 | 0.94 | 0.94 | -137 | 855.871 | 718.871 | 0% | 21 | 74% | 1 | 19222 | 1870.9241 |  | #REF! |  | 3 | 285.2903 | 35.9%
2021-05-12 | 225 | 4841.129 | 225 | 4841.129 | 225 | 4841.129 | 225 | 4841.129 | 225 | 4841.129 | 225 | 4841.129 | 225 | 4841.129 | 225 | 4841.129 | 225 | 4841.129 | 225 | 4841.129 | 225 | 4841.129 | 72.58% | 53252.4194 | 232 | 2320 | 232 | 2320 | 232 | 2320 | 232 | 2320 | 232 | 2320 | 232 | 2320 | 232 | 2320 | 82.86% | 16240 | 74.75% | 69492.4194 | -2760.0968 |  |  | 0.94 | -154 | -2606.0968 | -2760.0968 | 0% | 22 | 68% | 0 | 19222 | 1725.7595 |  | #REF!
2021-05-13 | 218 | 4690.5161 | 218 | 4690.5161 | 218 | 4690.5161 | 218 | 4690.5161 | 218 | 4690.5161 | 218 | 4690.5161 | 218 | 4690.5161 | 218 | 4690.5161 | 218 | 4690.5161 | 218 | 4690.5161 | 218 | 4690.5161 | 70.32% | 51595.6774 | 224 | 2240 | 224 | 2240 | 224 | 2240 | 224 | 2240 | 224 | 2240 | 224 | 2240 | 224 | 2240 | 80% | 15680 | 72.36% | 67275.6774 | -2216.7419 |  |  | 0.94 | -115 | -2101.7419 | -2216.7419 | 0% | 21 | 74% | 0 | 19222 | 1386.0127 |  | #REF!
2021-05-14 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 212 | 4561.4194 | 68.39% | 50175.6129 | 218 | 2180 | 218 | 2180 | 218 | 2180 | 218 | 2180 | 218 | 2180 | 218 | 2180 | 218 | 2180 | 77.86% | 15260 | 70.38% | 65435.6129 | -1840.0645 |  |  | 0.94 | -89 | -1751.0645 | -1840.0645 | 0% | 22.5 | 67% | 0 | 19222 | 1646.2278 |  | #REF!
2021-05-15 | 206 | 4432.3226 | 206 | 4432.3226 | 206 | 4432.3226 | 206 | 4432.3226 | 206 | 4432.3226 | 206 | 4432.3226 | 206 | 4432.3226 | 206 | 4432.3226 | 206 | 4432.3226 | 206 | 4432.3226 | 206 | 4432.3226 | 66.45% | 48755.5484 | 213 | 2130 | 213 | 2130 | 213 | 2130 | 213 | 2130 | 213 | 2130 | 213 | 2130 | 213 | 2130 | 76.07% | 14910 | 68.48% | 63665.5484 | -1770.0645 |  |  | 0.94 | -139 | -1631.0645 | -1770.0645 | 0% | 23.5 | 65% | 0 | 19222 | 1293.3544 |  | #REF!
2021-05-16 | 195 | 4195.6452 | 195 | 4195.6452 | 195 | 4195.6452 | 195 | 4195.6452 | 195 | 4195.6452 | 195 | 4195.6452 | 195 | 4195.6452 | 195 | 4195.6452 | 195 | 4195.6452 | 195 | 4195.6452 | 195 | 4195.6452 | 62.9% | 46152.0968 | 201 | 2010 | 201 | 2010 | 201 | 2010 | 201 | 2010 | 201 | 2010 | 201 | 2010 | 201 | 2010 | 71.79% | 14070 | 64.78% | 60222.0968 | -3443.4516 |  |  | 0.94 | -115 | -3328.4516 | -3443.4516 | 0% | 21.5 | 75% | 0 | 19222 | 2417.3502 |  | #REF!
2021-05-17 | 188 | 4045.0323 | 188 | 4045.0323 | 188 | 4045.0323 | 188 | 4045.0323 | 188 | 4045.0323 | 188 | 4045.0323 | 188 | 4045.0323 | 188 | 4045.0323 | 188 | 4045.0323 | 188 | 4045.0323 | 188 | 4045.0323 | 60.65% | 44495.3548 | 194 | 1940 | 194 | 1940 | 194 | 1940 | 194 | 1940 | 194 | 1940 | 194 | 1940 | 194 | 1940 | 69.29% | 13580 | 62.47% | 58075.3548 | -2146.7419 |  |  | 0.94 | -93 | -2053.7419 | -2146.7419 | 0% | 22.5 | 70% | 0 | 19222 | 2261.6329 |  | #REF!
2021-05-18 | 179 | 3851.3871 | 179 | 3851.3871 | 179 | 3851.3871 | 179 | 3851.3871 | 179 | 3851.3871 | 179 | 3851.3871 | 179 | 3851.3871 | 179 | 3851.3871 | 179 | 3851.3871 | 179 | 3851.3871 | 179 | 3851.3871 | 57.74% | 42365.2581 | 186 | 1860 | 186 | 1860 | 186 | 1860 | 186 | 1860 | 186 | 1860 | 186 | 1860 | 186 | 1860 | 66.43% | 13020 | 59.57% | 55385.2581 | -2690.0968 |  |  | 0.94 | -136 | -2554.0968 | -2690.0968 | 0% | 23 | 34% | 0 | 19222 | 3151.9241 |  | #REF!
2021-05-19 | 170 | 3657.7419 | 170 | 3657.7419 | 170 | 3657.7419 | 170 | 3657.7419 | 170 | 3657.7419 | 170 | 3657.7419 | 170 | 3657.7419 | 170 | 3657.7419 | 170 | 3657.7419 | 170 | 3657.7419 | 170 | 3657.7419 | 54.84% | 40235.1613 | 178 | 1780 | 178 | 1780 | 178 | 1780 | 178 | 1780 | 178 | 1780 | 178 | 1780 | 178 | 1780 | 63.57% | 12460 | 56.68% | 52695.1613 | -2690.0968 |  |  | 0.94 | -95 | -2595.0968 | -2690.0968 | 0% | 23 | 73% | 0 | 19222 | 1888.4262 |  | #REF!
2021-05-20 | 203 | 4367.7742 | 203 | 4367.7742 | 203 | 4367.7742 | 203 | 4367.7742 | 203 | 4367.7742 | 203 | 4367.7742 | 203 | 4367.7742 | 203 | 4367.7742 | 203 | 4367.7742 | 203 | 4367.7742 | 203 | 4367.7742 | 65.48% | 48045.5161 | 210 | 2100 | 210 | 2100 | 210 | 2100 | 210 | 2100 | 210 | 2100 | 210 | 2100 | 210 | 2100 | 75% | 14700 | 67.49% | 62745.5161 | -1618.4452 | 11668.8 | 1.003 | 1.003 | -63 | -1555.4452 | -1618.4452 | 0% | 23.5 | 77% | 1 | 19222 | 2046.7173 |  | #REF!
2021-05-21 | 194 | 4174.129 | 194 | 4174.129 | 194 | 4174.129 | 194 | 4174.129 | 194 | 4174.129 | 194 | 4174.129 | 194 | 4174.129 | 194 | 4174.129 | 194 | 4174.129 | 194 | 4174.129 | 194 | 4174.129 | 62.58% | 45915.4194 | 201 | 2010 | 201 | 2010 | 201 | 2010 | 201 | 2010 | 201 | 2010 | 201 | 2010 | 201 | 2010 | 71.79% | 14070 | 64.52% | 59985.4194 | -2760.0968 |  |  | 1.003 | -209 | -2551.0968 | -2760.0968 | 0% | 24.5 | 47% | 0 | 19222 | 2714.6287 |  | #REF!
2021-05-22 | 182 | 3915.9355 | 182 | 3915.9355 | 182 | 3915.9355 | 182 | 3915.9355 | 182 | 3915.9355 | 182 | 3915.9355 | 182 | 3915.9355 | 182 | 3915.9355 | 182 | 3915.9355 | 182 | 3915.9355 | 182 | 3915.9355 | 58.71% | 43075.2903 | 189 | 1890 | 189 | 1890 | 189 | 1890 | 189 | 1890 | 189 | 1890 | 189 | 1890 | 189 | 1890 | 67.5% | 13230 | 60.56% | 56305.2903 | -3680.129 |  |  | 1.003 | -129 | -3551.129 | -3680.129 | 0% | 24.5 | 50% | 0 | 19222 | 1424.6203 |  | #REF!
2021-05-23 | 176 | 3786.8387 | 176 | 3786.8387 | 176 | 3786.8387 | 176 | 3786.8387 | 176 | 3786.8387 | 176 | 3786.8387 | 176 | 3786.8387 | 176 | 3786.8387 | 176 | 3786.8387 | 176 | 3786.8387 | 176 | 3786.8387 | 56.77% | 41655.2258 | 182.5 | 1825 | 182.5 | 1825 | 182.5 | 1825 | 182.5 | 1825 | 182.5 | 1825 | 182.5 | 1825 | 182.5 | 1825 | 65.18% | 12775 | 58.55% | 54430.2258 | -1875.0645 |  |  | 1.003 | -69 | -1806.0645 | -1875.0645 | 0% | 23.5 | 55% | 0 | 19222 | 3205.4599 |  | #REF!
2021-05-24 | 208 | 4475.3548 | 208 | 4475.3548 | 208 | 4475.3548 | 208 | 4475.3548 | 208 | 4475.3548 | 208 | 4475.3548 | 208 | 4475.3548 | 208 | 4475.3548 | 208 | 4475.3548 | 208 | 4475.3548 | 208 | 4475.3548 | 67.1% | 49228.9032 | 215 | 2150 | 215 | 2150 | 215 | 2150 | 215 | 2150 | 215 | 2150 | 215 | 2150 | 215 | 2150 | 76.79% | 15050 | 69.14% | 64278.9032 | -2211.3226 | 12060 | 1.003 | 1.003 | -211.2 | -2000.1226 | -2211.3226 | 0% | 24.5 | 55% | 1 | 19222 | 1589.346 |  | #REF!
2021-05-25 | 201 | 4324.7419 | 201 | 4324.7419 | 201 | 4324.7419 | 201 | 4324.7419 | 201 | 4324.7419 | 201 | 4324.7419 | 201 | 4324.7419 | 201 | 4324.7419 | 201 | 4324.7419 | 201 | 4324.7419 | 201 | 4324.7419 | 64.84% | 47572.1613 | 208 | 2080 | 208 | 2080 | 208 | 2080 | 208 | 2080 | 208 | 2080 | 208 | 2080 | 208 | 2080 | 74.29% | 14560 | 66.83% | 62132.1613 | -2146.7419 |  |  | 1.003 | -90 | -2056.7419 | -2146.7419 | 0% | 24.5 | 66% | 0 | 19222 | 3368.1266 |  | #REF!
2021-05-26 | 187 | 4023.5161 | 187 | 4023.5161 | 187 | 4023.5161 | 187 | 4023.5161 | 187 | 4023.5161 | 187 | 4023.5161 | 187 | 4023.5161 | 187 | 4023.5161 | 187 | 4023.5161 | 187 | 4023.5161 | 187 | 4023.5161 | 60.32% | 44258.6774 | 194 | 1940 | 194 | 1940 | 194 | 1940 | 194 | 1940 | 194 | 1940 | 194 | 1940 | 194 | 1940 | 69.29% | 13580 | 62.21% | 57838.6774 | -4293.4839 |  |  | 1.003 | -114 | -4179.4839 | -4293.4839 | 0% | 24.5 | 65% | 0 | 19222 | 2428.6751 |  | #REF!
2021-05-27 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 57.1% | 41891.9032 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 65.71% | 12880 | 58.91% | 54771.9032 | -3066.7742 |  |  | 1.003 | -106 | -2960.7742 | -3066.7742 | 0% | 23.5 | 60% | 0 | 19222 | 0 |  | #REF!
2021-05-28 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 57.1% | 41891.9032 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 65.71% | 12880 | 58.91% | 54771.9032 | 0 |  |  | 1.003 | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 19222 | #REF! |  | #REF!
2021-05-29 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 57.1% | 41891.9032 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 65.71% | 12880 | 58.91% | 54771.9032 | 0 |  |  | 1.003 | 0 | 0 | 0 | 0% | 0 | 0%
2021-05-30 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 57.1% | 41891.9032 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 65.71% | 12880 | 58.91% | 54771.9032 | 0 |  |  | 1.003 | 0 | 0 | 0 | 0% | 0 | 0%
2021-05-31 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 177 | 3808.3548 | 57.1% | 41891.9032 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 184 | 1840 | 65.71% | 12880 | 58.91% | 54771.9032 | 0 |  |  | 1.003 | 0 | 0 | 0 | 0% | 0 | 0%
[42 empty] | NB delivery | 3 | 38273.8 | 0.982 |  |  | -53734.6 | -57217.8
37584.8716
-2119.1778
43309
-1.2407

## EDl log
Date | EDL | Conso EDL KW |  |  | Peak | 320 | Day | 112 | Night | 80
[11 empty] | P | D | N | fee | T EDL | Gen | Elc C
2021-04-30 | 1008810 | 1767 | 1767 | 1008810 | 150653 | 103 | 492400 | 690 | 365756 | 974 | 21.864 | 51.2637 | 51.6882 | 159.9631 | 284.7791 | 1348.3239 | 1633.1029 | 7873 | 0.20743 |  |  |  |  | VAT | 0.1
2021-05-01 | 1011197 | 2387 | 2388 | 1011198 | 151092 | 439 | 493608 | 1208 | 366497 | 741 | 93.1874 | 89.7486 | 39.3234 | 154.803 | 377.0624 | 1314.2961 | 1691.3585 | 8346 | 0.20265 | EDL | 2021-04-01 |  |  | Subscription
2021-05-02 | 1013614 | 2417 | 2416 | 1013613 | 151431 | 339 | 494679 | 1071 | 367503 | 1006 | 71.9602 | 79.5701 | 53.3864 | 154.803 | 359.7198 | 684.4857 | 1044.2055 | 6548 | 0.15947 |  |  |  |  | KVA | 5000
2021-05-03 | 1015880 | 2266 | 2267 | 1015881 | 151769 | 338 | 495673 | 994 | 368438 | 935 | 71.7479 | 73.8494 | 49.6186 | 154.803 | 350.019 | 833.7497 | 1183.7686 | 7179 | 0.16489
2021-05-04 | 1017767 | 1887 | 1886 | 1017766 | 151883 | 114 | 496424 | 751 | 369459 | 1021 | 24.199 | 55.7957 | 54.1824 | 154.803 | 288.9802 | 1644.9134 | 1933.8935 | 8383 | 0.23069 | Electricity consumption |  | Price LL
2021-05-05 | 1019853 | 2086 | 2085 | 1019852 | 152275 | 392 | 497192 | 768 | 370384 | 925 | 83.2106 | 57.0587 | 49.0879 | 154.803 | 344.1603 | 1714.6354 | 2058.7956 | 4768 | 0.43179 | Index in | Index Out |  | Kwh Cost | K | Kwh | Total cost LL | Fees
2021-05-06 | 1021807 | 1954 | 1955 | 1021808 | 152555 | 280 | 498020 | 828 | 371231 | 847 | 59.4362 | 61.5164 | 44.9486 | 154.803 | 320.7042 | 983.6789 | 1304.3831 | 3912 | 0.33343 | 344256 | 365756 | Night | 80 | 1 | 21500 | 1720000 | 1033333 | 41.22%
2021-05-07 | 1023553 | 1746 | 1747 | 1023554 | 152749 | 194 | 498840 | 820 | 371964 | 733 | 41.1808 | 60.9221 | 38.8988 | 154.803 | 295.8047 | 1945.0886 | 2240.8933 | 8995.4 | 0.24912 | 468436 | 492400 | day | 112 | 1 | 23964 | 2683968 | 6200000 | 45.95%
2021-05-08 | 1025137 | 1584 | 1583 | 1025136 | 152844 | 95 | 499520 | 680 | 372772 | 808 | 20.1658 | 50.5207 | 42.8789 | 154.803 | 268.3685 | 1954.9086 | 2223.2771 | 8249.8 | 0.26949 | 143963 | 150653 | Peak | 320 | 1 | 6690 | 2140800 | 1000 | 12.83% | 107040 | 474034.2857
2021-05-09 | 1026689 | 1552 | 1553 | 1026690 | 153110 | 266 | 500136 | 616 | 373443 | 671 | 56.4643 | 45.7658 | 35.6086 | 154.803 | 292.6418 | 1765.6994 | 2058.3412 | 9025.8 | 0.22805 | [5 empty] | 52154
2021-05-10 | 1028463 | 1774 | 1773 | 1028462 | 153293 | 183 | 500776 | 640 | 374393 | 950 | 38.8458 | 47.5489 | 50.4146 | 154.803 | 291.6123 | 2191.2538 | 2482.8661 | 9481 | 0.26188 | Occ % | 0% |  | Per G |  |  | 6544768
2021-05-11 | 1030266 | 1803 | 1802 | 1030265 | 153429 | 136 | 501555 | 779 | 375280 | 887 | 28.869 | 57.876 | 47.0713 | 154.803 | 288.6193 | -840.4653 | -551.846 | 9028 | -0.061126 | Gen RH | 240 | 8 | 4 |  |  | 13779101 | 7234333
2021-05-12 | 1031515 | 1249 | 1250 | 1031516 | 153620 | 191 | 502210 | 655 | 375684 | 404 | 40.5439 | 48.6633 | 21.4395 | 154.803 | 265.4498 | 2559.187 | 2824.6368 | 9411 | 0.30014 | H Deg | -30.3
2021-05-13 | 1033182 | 1667 | 1667 | 1033182 | 153788 | 168 | 503101 | 891 | 376292 | 608 | 35.6617 | 66.197 | 32.2653 | 154.803 | 288.9271 | 2063.9106 | 2352.8377 | 9646 | 0.24392 | C Deg | 45.4 |  |  |  |  | 9140.3655
2021-05-14 | 1035109 | 1927 | 1927 | 1035109 | 153788 | 0 | 503838 | 737 | 377482 | 1190 | 0 | 54.7556 | 63.1509 | 154.803 | 272.7095 | 1719.5454 | 1992.2549 | 8868 | 0.22466 |  |  |  |  | Vat | 11% |  | 0
2021-05-15 | 1036805 | 1696 | 1696 | 1036805 | 154064 | 276 | 504573 | 735 | 378167 | 685 | 58.5871 | 54.607 | 36.3516 | 154.803 | 304.3486 | 1601.7054 | 1906.054 | 7587 | 0.25123 | [7 empty] | 0
2021-05-16 | 1037502 | 697 | 697 | 1037502 | 154300 | 236 | 504800 | 227 | 378401 | 234 | 50.0962 | 16.865 | 12.4179 | 154.803 | 234.1821 | 3268.5395 | 3502.7216 | 12839 | 0.27282 | [7 empty] | 0
2021-05-17 | 1039767 | 2265 | 2264 | 1039766 | 154501 | 201 | 506049 | 1249 | 379215 | 814 | 42.6667 | 92.7947 | 43.1973 | 154.803 | 333.4617 | 2016.7746 | 2350.2363 | 10089 | 0.23295 | Before new counter
2021-05-18 | 1041509 | 1742 | 1743 | 1041510 | 154501 | 0 | 506766 | 717 | 380241 | 1026 | 0 | 53.2697 | 54.4478 | 154.803 | 262.5205 | 2508.123 | 2770.6435 | 10297 | 0.26907 | EDL | 2021-05-01 |  |  | Subscription
2021-05-19 | 1043337 | 1828 | 1828 | 1043337 | 154650 | 149 | 507784 | 1018 | 380902 | 661 | 31.6285 | 75.6325 | 35.0779 | 154.803 | 297.142 | 2548.385 | 2845.527 | 15339 | 0.18551 |  |  |  |  | KVA | 5000
2021-05-20 | 1044257 | 920 | 920 | 1044257 | 154650 | 0 | 508523 | 739 | 381083 | 181 | 0 | 54.9041 | 9.6053 | 154.803 | 219.3125 | 1527.4471 | 1746.7596 | 8897 | 0.19633
2021-05-21 | 1045564 | 1307 | 1307 | 1045564 | 154794 | 144 | 509013 | 490 | 381756 | 673 | 30.5672 | 36.4046 | 35.7148 | 154.803 | 257.4896 | 2505.177 | 2762.6666 | 10235 | 0.26992 | Electricity consumption |  | Price LL
2021-05-22 | 1046532 | 968 | 968 | 1046532 | 154794 | 0 | 509781 | 768 | 381956 | 200 | 0 | 57.0587 | 10.6136 | 154.803 | 222.4753 | 3487.2087 | 3709.6841 | 12191 | 0.3043 | Index in | Index Out |  | Kwh Cost | K | Kwh | Total cost LL | Fees
2021-05-23 | 1048219 | 1687 | 1688 | 1048220 | 155137 | 343 | 510531 | 750 | 382551 | 595 | 72.8093 | 55.7214 | 31.5755 | 154.803 | 314.9092 | 1773.5554 | 2088.4645 | 8568 | 0.24375 | 365756 | 384519 | Night | 80 | 1 | 18763 | 1501040 | 1033333 | 42.33%
2021-05-24 | 1049003 | 784 | 790 | 1049009 | 155137 | 0 | 511109 | 578 | 382763 | 212 | 0 | 42.9426 | 11.2504 | 154.803 | 208.9961 | 1964.1204 | 2173.1164 | 13728 | 0.1583 | 492400 | 513001 | day | 112 | 1 | 20601 | 2307312 | 6200000 | 46.48%
2021-05-25 | 1050985 | 1982 | 1976 | 1050979 | 155451 | 314 | 511868 | 759 | 383666 | 903 | 66.6534 | 56.39 | 47.9204 | 154.803 | 325.7669 | 2019.7206 | 2345.4875 | 9803 | 0.23926 | 150653 | 155610 | Peak | 320 | 1 | 4957 | 1586240 | 1000 | 11.18% | 79312 | 351238.8571
2021-05-26 | 1051724 | 739 | 728 | 1051713 | 155451 | 0 | 512392 | 524 | 383870 | 204 | 0 | 38.9307 | 10.8259 | 154.803 | 204.5596 | 4104.2532 | 4308.8128 | 14177 | 0.30393 | [5 empty] | 44321 |  | 7234333
2021-05-27 | 1053131 | 1407 | 1417 | 1053141 | 155610 | 159 | 513001 | 609 | 384519 | 649 | 33.7512 | 45.2458 | 34.4411 | 154.803 | 268.2412 | 2907.4803 | 3175.7214 | 11827 | 0.26851 | Occ % | 0% |  | Per G |  |  | 5394592
2021-05-28 | 1053131 | 0 | 0 | 1053131 | 155610 | 0 | 513001 | 0 | 384519 | 0 | 0 | 0 | 0 | 154.803 | 154.803 | 0 | 154.803 | 0 | 0
2021-05-29 | 1053131 | 0 | 0 | 1053131 | 155610 | 0 | 513001 | 0 | 384519 | 0 | 0 | 0 | 0 | 154.803 | 154.803 | 0 | 154.803 | 0 | 0
2021-05-30 | 1053131 | 0 | 0 | 1053131 | 155610 | 0 | 513001 | 0 | 384519 | 0 | 0 | 0 | 0 | 154.803 | 154.803 | 0 | 154.803 | 0 | 0 | Gen RH | 274 | 10.1481 | 10.1481 |  |  | 12628925 | 7234333
2021-05-31 | 1053131 | 0 | 0 | 1053131 | 155610 | 0 | 513001 | 0 | 384519 | 0 | 0 | 0 | 0 | 154.803 | 154.803 | 0 | 154.803 | 0 | 0 | Gen RH | [5 empty] | 0 | 0
27 |  | 1641.5185 |  |  |  | 183.5926 |  | 763 |  | 694.9259 | 0 | 0 | 0 | 233365.5806 | [13 empty] | 480049%
|  | 100% |  |  |  | 11.18% |  | 46.48% |  | 42.33% | [14 empty] | $ | 8377.3964
31
8377.3964
Note on A19: suzan.abousleiman: records are not taken neither recorded - they copy paste 15th May record to 16th on the excel sheet they work on (Fixed manually)

## General information
GENERAL & HOTEL'S INFORMATION SHEET
| Max Temp | MIN TEMP | AVE TEMP | AVE Humidity | AVE OCC | # of OCC Rooms | Ball room | Meeting rooms | Outlets | Total covers | # of permenant Emp | # of casuals | Total # of EMP | # of EMP/OCC Room
2021-04-30 | 25 | 21 | 23 | 56% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-01 | 26 | 21 | 23.5 | 65% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-02 | 25 | 21 | 23 | 67% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-03 | 26 | 22 | 24 | 65% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-04 | 26 | 19 | 22.5 | 44% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-05 | 24 | 22 | 23 | 53% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-06 | 24 | 20 | 22 | 64% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-07 | 25 | 21 | 23 | 65% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-08 | 29 | 20 | 24.5 | 52% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-09 | 28 | 21 | 24.5 | 55% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-10 | 24 | 20 | 22 | 53% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-11 | 24 | 18 | 21 | 74% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-12 | 25 | 19 | 22 | 68% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-13 | 24 | 18 | 21 | 74% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-14 | 24 | 21 | 22.5 | 67% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-15 | 25 | 22 | 23.5 | 65% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-16 | 24 | 19 | 21.5 | 75% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-17 | 25 | 20 | 22.5 | 70% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-18 | 32 | 14 | 23 | 34% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-19 | 26 | 20 | 23 | 73% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-20 | 26 | 21 | 23.5 | 77% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-21 | 25 | 24 | 24.5 | 47% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-22 | 26 | 23 | 24.5 | 50% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-23 | 25 | 22 | 23.5 | 55% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-24 | 26 | 23 | 24.5 | 55% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-25 | 27 | 22 | 24.5 | 66% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-26 | 26 | 23 | 24.5 | 65% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-27 | 25 | 22 | 23.5 | 60% | 0% | 0 | 0 | 0 | 0 | 0
2021-05-28 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0
2021-05-29 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0
2021-05-30 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0
2021-05-31 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0
[5 empty] | 0% | 0
23.1481
http://www.accuweather.com/en/lb/lebanon-weather

## Sheet1 (hidden)
TOTAL CH RH | TOTAL CH cons KW | TOTAL ELIC KW | TOTAL EDL | TOTAL GEN KW | GEN HR | WATER IN | TOTAL CT | TOTAL WATER | Date
#VALUE! | 1032 | 8346 | 4419 | 3927 | 8 | 0 | 0 | -20.9 | 2021-04-30
7 | 579 | 6548 | 4552 | 1996 | 6 | 7 | 0 | -19.2 | 2021-05-01
5 | 993 | 7179 | 4159 | 3020 | 3 | 0 | 3 | 94.6 | 2021-05-02
5 | 1269 | 8383 | 4172 | 4211 | 4 | 289 | 0 | -232.6 | 2021-05-03
9 | 1788 | 4768 | -5779 | 10547 | 8 | 0 | 0 | 71.6 | 2021-05-04
4 | 926 | 3912 | 430 | 3482 | 9 | 295 | 0 | -235.6 | 2021-05-05
8 | 1572 | 8995.4 | 3140.4 | 5855 | 6 | 0 | 6 | 49 | 2021-05-06
7 | 1551 | 8249.8 | 2740.8 | 5509 | 8.5 | 293 | 0 | -258.9 | 2021-05-07
8 | 1818 | 9025.8 | 2722.8 | 6303 | 8.6 | 0 | 0 | 83.4 | 2021-05-08
8 | 2061 | 9481 | 3143 | 6338 | 8.9 | 0 | 2 | -15 | 2021-05-09
7 | 1422 | 9028 | 3284 | 5744 | 9 | 0 | 0 | -65.8 | 2021-05-10
9 | 2171 | 9411 | 2142 | 7269 | 10 | 0 | 0 | -30.5 | 2021-05-11
8 | 1981 | 9646 | 2941 | 6705 | 12 | 0 | 0 | -47.5 | 2021-05-12
8 | 1684 | 8868 | 3483 | 5385 | 9 | 341 | 0 | -374 | 2021-05-13
5 | 1169 | 7587 | 1191 | 6396 | 10 | 0 | 0 | -25.4 | 2021-05-14
11 | 2663 | 12839 | 7814 | 5025 | 7 | 0 | 0 | -51.5 | 2021-05-15
10 | 2275 | 10089 | 697 | 9392 | 16 | 0 | 4 | -50.4 | 2021-05-16
11 | 2111 | 10297 | 1510 | 8787 | 9 | 0 | 0 | -56 | 2021-05-17
10 | 2132 | 15339 | 3093 | 12246 | 11 | 0 | 2 | -115.6 | 2021-05-18
15 | 3025 | 8897 | 1560 | 7337 | 16 | 0 | 1 | -44.6 | 2021-05-19
9 | 1961 | 10235 | 2283 | 7952 | 10 | 0 | 0 | 22.1 | 2021-05-20
14 | 2509 | 12191 | 1644 | 10547 | 12 | 0 | 0 | -19.6 | 2021-05-21
7 | 1414 | 8568 | 3033 | 5535 | 16 | 0 | 1 | -19.6 | 2021-05-22
16 | 3143 | 13728 | 1274 | 12454 | 8 | 0 | 0 | 26.8 | 2021-05-23
7 | 1575 | 9803 | 3628 | 6175 | 17 | 0 | 0 | -10.7 | 2021-05-24
16 | 2970 | 14177 | 1091 | 13086 | 9 | 0 | 0 | -52.7 | 2021-05-25
11 | 2860 | 11827 | 2391 | 9436 | 18 | 0 | 3 | 62.5 | 2021-05-26
0 | 0 | 0 | 0 | 0 | 13 | 435 | 0 | -401.3 | 2021-05-27
#REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | #REF! | 2021-05-28
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## Report (hidden)
| Boiler Fuel | Steam Fuel | GEN FUEL | FUEL TOTAL | CT/mᶾ | Water Consumption | Chiller KW | GEN KW | EDL KW | occ | covers | temp. C⁰ | RH %
| 0 | 0 |  | 0
2016-11-30 | 810 | -606.1 | 1420.5021 | 1624.4021 | 106 | -58.4 | 6284 | 2399 | 23932 | 0 | 0 | 0 | 0
2021-05-01 | 195 | 0 | 1010.7468 | 1205.7468 | 0 | -22.8 | 1032 | 3927 | 4419
2021-05-02 | 153 | 0 | 513.7384 | 666.7384 | 0 | -7.1 | 579 | 1996 | 4552
2021-05-03 | 141 | 0 | 777.2996 | 918.2996 | 3 | -4.2 | 993 | 3020 | 4159
2021-05-04 | 95 | 0 | 1083.8439 | 1178.8439 | 0 | 99.7 | 1269 | 4211 | 4172
2021-05-05 | 164 | 0 | 1443.9241 | 1607.9241 | 0 | -28 | 1788 | 5610 | -842
2021-05-06 | 155 | 0 | 896.211 | 1051.211 | 0 | 84.3 | 926 | 3482 | 430
2021-05-07 | 166 | 0 | 1506.9831 | 1672.9831 | 6 | -5.1 | 1572 | 5855 | 3140.4
2021-05-08 | 156 | 0 | 1417.9283 | 1573.9283 | 0 | 54.1 | 1551 | 5509 | 2740.8
2021-05-09 | 112 | 0 | 1622.2911 | 1734.2911 | 0 | -36.2 | 1818 | 6303 | 2722.8
2021-05-10 | 82 | 0 | 1631.2996 | 1713.2996 | 2 | 94.4 | 2061 | 6338 | 3143
2021-05-11 | 81 | 56 | 1478.4135 | 1615.4135 | 0 | -14 | 1422 | 5744 | 3284
2021-05-12 | 154 | 0 | 1870.9241 | 2024.9241 | 0 | -47.3 | 2171 | 7269 | 2142
2021-05-13 | 115 | 0 | 1725.7595 | 1840.7595 | 0 | -15.6 | 1981 | 6705 | 2941
2021-05-14 | 89 | 0 | 1386.0127 | 1475.0127 | 0 | -31.9 | 1684 | 5385 | 3483
2021-05-15 | 139 | 0 | 1646.2278 | 1785.2278 | 0 | -1.1 | 1169 | 6396 | 1191
2021-05-16 | 115 | 0 | 1293.3544 | 1408.3544 | 0 | -24.3 | 2663 | 5025 | 7814
2021-05-17 | 93 | 0 | 2417.3502 | 2510.3502 | 4 | -27.2 | 2275 | 9392 | 697
2021-05-18 | 136 | 0 | 2261.6329 | 2397.6329 | 0 | -23.2 | 2111 | 8787 | 1510
2021-05-19 | 95 | 0 | 3151.9241 | 3246.9241 | 2 | -32.8 | 2132 | 12246 | 3093
2021-05-20 | 63 | 0 | 1888.4262 | 1951.4262 | 1 | -85.5 | 3025 | 7337 | 1560
2021-05-21 | 186 | 23 | 2046.7173 | 2255.7173 | 0 | -18.5 | 1961 | 7952 | 2283
2021-05-22 | 129 | 0 | 2714.6287 | 2843.6287 | 0 | 40.6 | 2509 | 10547 | 1644
2021-05-23 | 69 | 0 | 1424.6203 | 1493.6203 | 1 | -9.8 | 1414 | 5535 | 3033
2021-05-24 | 88 | 123.2 | 3205.4599 | 3416.6599 | 0 | -9.8 | 3143 | 12454 | 1274
2021-05-25 | 90 | 0 | 1589.346 | 1679.346 | 0 | 36.6 | 1575 | 6175 | 3628
2021-05-26 | 114 | 0 | 3368.1266 | 3482.1266 | 0 | -47.3 | 2970 | 13086 | 1091
2021-05-27 | 106 | 0 | 2428.6751 | 2534.6751 | 3 | -37.8 | 2860 | 9436 | 2391
2021-05-28 | 0 | 0 | 0 | 0 | 0 | 83.2 | 0 | 0 | 0
#REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## Sheet5 (hidden)
Outdoor conditions
Date | Total Boiler running H | AVE CONSUM | Total Steam running H | AVE CONSUM | Total GEN running H | AVE CONSUM | Actual Diesel Consumption | Actual Gas Consumption | Total ELEC power | Gen ELEC power | EDL ELEC power | Chillers running H | Total Water delivery | Total water consumption | Total water in tanks | Occupancy | AVE TEPM | AVE Humidity
2016-02-29 | 2 | 180 | 0 | 0 | 6
2016-03-01 | 1 | 90 | 0 | 0
2016-03-02 | 2 | 180 | 0 | 0
2016-03-03 | 3 | 270 | 0 | 0
2016-03-04 | 1 | 90 | 0 | 0
2016-03-05 | 2 | 180 | 0 | 0
2016-03-06 | 2 | 180 | 0 | 0
2016-03-07 | 2 | 180 | 0 | 0
2016-03-08 | 2 | 180 | 0 | 0
2016-03-09 | 2 | 180 | 0 | 0
2016-03-10 | 1 | 90 | 0 | 0
2016-03-11 | 1 | 90 | 0 | 0
2016-03-12 | 2 | 180 | 0 | 0
2016-03-13 | 1 | 90 | 0 | 0
2016-03-14 | 1 | 90 | 0 | 0
2016-03-15 | 2 | 180 | 0 | 0
2016-03-16 | 1 | 90 | 0 | 0
2016-03-17 | 1 | 90 | 0 | 0
2016-03-18 | 3 | 270 | 0 | 0
2016-03-19 | 1 | 90 | 0 | 0
2016-03-20 | 1 | 90 | 0 | 0
2016-03-21 | 1 | 90 | 1 | 107
2016-03-22 | 2 | 180 | 0 | 0
2016-03-23 | 1 | 90 | 0 | 0
2016-03-24 | 1 | 90 | 1 | 107
2016-03-25 | 1 | 90 | 0 | 0
2016-03-26 | 1 | 90 | 0 | 0
2016-03-27 | 2 | 180 | 0 | 0
2016-03-28 | 0 | 0 | 0 | 0
2016-03-29 | #REF! | #REF! | #REF! | #REF!
2016-03-30 | #REF! | #REF! | #REF! | #REF!
2016-03-31 | #REF! | #REF! | #REF! | #REF!
2016-04-01 | #REF! | #REF! | #REF! | #REF!

## Swimming Pool quality check
Date | Swimming Pool |  |  | Jacuzzi |  |  | Water meter SW Pool | Cons M3 | Time
| 1.0-1.5 | 7.2-7.4 |  | 3.5 | 7.2-7.4
| Chl | PH | T C | Chl | PH | T C
[7 empty] | 0 |  |  |  |  | Counter 1 | Counter 2 | Total
2021-04-30 | 1.5 | 8 |  | 0.5 | 8.2 |  | 6751 | 0 | 8:00 | 0 | 2021-04-30 | 6541 | 642 | 6836
2021-05-01 | 1.5 | 8 |  | 1 | 7.8 |  | 6751 | 0 | 7:00 |  | 2021-05-01 | 6543 | 487 | 7030
2021-05-02 | 1.2 | 8.2 |  | 1 | 7.8 |  | 6754 | 3 | 7:00 |  | 2021-05-02 | 6550 | 487 | 7037
2021-05-03 | 1.2 | 8.7 |  | 1 | 8.2 |  | 6754 | 0 | 7:00 |  | 2021-05-03 | 6555 | 487 | 7042
2021-05-04 | 1.2 | 8.7 |  | 1 | 8.2 |  | 6754 | 0 | 6:00 |  | 2021-05-04 | 6555 | 487 | 7042
2021-05-05 | 1.2 | 8 |  | 1 | 8.2 |  | 6754 | 0 | 7:00 |  | 2021-05-05 | 6555 | 487 | 7042
2021-05-06 | 1.5 | 8 |  | 1 | 8.2 |  | 6760 | 6 | 7:00 |  | 2021-05-06 | 6555 | 487 | 7042
2021-05-07 | 1.5 | 8 |  | 1 | 8.3 |  | 6760 | 0 | 7:00 |  | 2021-05-07 | 6555 | 487 | 7042
2021-05-08 | 1.5 | 8.7 |  | 1 | 8.7 |  | 6760 | 0 | 7:00 |  | 2021-05-08 | 6555 | 487 | 7042
2021-05-09 | 1.4 | 8.4 |  | 1 | 8.3 |  | 6762 | 2 | 7:00 |  | 2021-05-09 | 6555 | 487 | 7042
2021-05-10 | 1.5 | 9.5 |  | 1 | 9.5 |  | 6762 | 0 | 7:00 |  | 2021-05-10 | 6555 | 487 | 7042
2021-05-11 | 1 | 9.5 |  | 0.9 | 9.5 |  | 6762 | 0 | 7:00 |  | 2021-05-11 | 6555 | 487 | 7042
2021-05-12 | 1 | 1.5 |  | 0.7 | 9.5 |  | 6762 | 0 | 7:00 |  | 2021-05-12 | 6555 | 487 | 7042
2021-05-13 | 1 | 1.5 |  | 0 | 9.5 |  | 6762 | 0 | 7:00 |  | 2021-05-13 | 6555 | 487 | 7042
2021-05-14 | 1 | 9.5 |  | 0 | 9.5 |  | 6762 | 0 | 7:00 |  | 2021-05-14 | 6555 | 487 | 7042
2021-05-15 | 1 | 9.5 |  | 0 | 9.5 |  | 6762 | 0 | 7:00 |  | 2021-05-15 | 6555 | 645 | 7200
2021-05-16 | 0.9 | 9 |  | 0 | 9 |  | 6766 | 4 | 2:00:00AM |  | 2021-05-16 | 6555 | 645 | 7200
2021-05-17 | 0.9 | 9 |  | 0 | 9 |  | 6766 | 0 | 7:00 |  | 2021-05-17 | 6555 | 645 | 7200
2021-05-18 | 0.5 | 9.5 |  | 0 | 10 |  | 6768 | 2 | 7:00 |  | 2021-05-18 | 6555 | 645 | 7200
2021-05-19 | 0,4 | 9.5 |  | 0 | 10 |  | 6769 | 1 | 7:00 |  | 2021-05-19 | 6555 | 645 | 7200
2021-05-20 | 1.5 | 8 |  | 1 | 7.8 |  | 6769 | 0 | 7:00 |  | 2021-05-20 | 6555 | 645 | 7200
2021-05-21 | 1.5 | 7.8 |  | 0.9 | 8 |  | 6769 | 0 | 7:00 |  | 2021-05-21 | 6555 | 645 | 7200
2021-05-22 | 1.5 | 7.8 |  | 1 | 8 |  | 6770 | 1 | 7:00 |  | 2021-05-22 | 6555 | 645 | 7200
2021-05-23 | 1.5 | 7.8 |  | 1 | 8 |  | 6770 | 0 | 7:00 |  | 2021-05-23 | 6555 | 645 | 7200
2021-05-24 | 1.5 | 7.8 |  | 1 | 8 |  | 6770 | 0 | 7:00 |  | 2021-05-24 | 6555 | 645 | 7200
2021-05-25 | 1.5 | 7.8 |  | 1 | 8 |  | 6770 | 0 | 7:00 |  | 2021-05-25 | 6555 | 645 | 7200
2021-05-26 | 1.5 | 7.8 |  | 1 | 8 |  | 6773 | 3 | 7:00 |  | 2021-05-26 | 6555 | 645 | 7200
2021-05-27 | 1.5 | 7.8 |  | 1 | 8 |  | 6773 | 0 | 7:00 |  | 2021-05-27 | 6555 | 645 | 7200
2021-05-28 | [6 empty] | 6773 | 0 | 7:00 |  | 2021-05-28 | 6555 | 645 | 7200
2021-05-29 | [6 empty] | 6773 | 0 | 8:00 |  | 2021-05-29 | 6555 | 646 | 7201
2021-05-30 | [6 empty] | 6773 | 0 | 9:00 |  | 2021-05-30 | 6555 | 647 | 7202
2021-05-31 | [6 empty] | 6773 | 0 | 10:00 |  | 2021-05-31 | 6555 | 648 | 7203
Note on N20: ahmad.ghazalah: Start refilling the pool

## Degree Days 2020
Four Seasons Hotel Beirut
Annual Utility consumption report
( Heating Degree Days / Cooling Degree Days ) 2020
LOCATION: |  | Four Seasons Beirut
JAN | Max (A) | Min (B) | (A+B)/2 -18.3=(C) | Feb | Max (A) | Min (B) | (A+B)/2 -18.3=(C) | Mar | Max (A) | Min (B) | (A+B)/2 -18.3=(C) | Apr | Max (A) | Min (B) | (A+B)/2 -18.3=(C) | May | Max (A) | Min (B) | (A+B)/2 -18.3=(C) | Jun | Max (A) | Min (B) | (A+B)/2 -18.3=(C) |  | Heating degree days | Cooling degree days
1 | 20 | 15 | -0.8 | 1 | 21 | 16 | 0.2 | 1 | 18 | 14 | -2.3 | 1 | 17 | 12 | -3.8 | 1 | 26 | 21 | 5.2 | 1 |  |  | -18.3 | Jan | -92.6 | 2.8
2 | 21 | 15 | -0.3 | 2 | 23 | 17 | 1.7 | 2 | 18 | 13 | -2.8 | 2 | 15 | 12 | -4.8 | 2 | 25 | 21 | 4.7 | 2 |  |  | -18.3 | Feb | -75.9 | 6.5
3 | 21 | 16 | 0.2 | 3 | 20 | 15 | -0.8 | 3 | 18 | 13 | -2.8 | 3 | 19 | 15 | -1.3 | 3 | 26 | 22 | 5.7 | 3 |  |  | -18.3 | Mar | -56.9 | 11.5
4 | 22 | 15 | 0.2 | 4 | 20 | 15 | -0.8 | 4 | 18 | 13 | -2.8 | 4 | 18 | 15 | -1.8 | 4 | 26 | 19 | 4.2 | 4 |  |  | -18.3 | Apr | -30.3 | 55.3
5 | 22 | 16 | 0.7 | 5 | 20 | 15 | -0.8 | 5 | 19 | 12 | -2.8 | 5 | 19 | 15 | -1.3 | 5 | 24 | 22 | 4.7 | 5 |  |  | -18.3 | May | -73.2 | 130.9
6 | 22 | 15 | 0.2 | 6 | 19 | 15 | -1.3 | 6 | 18 | 14 | -2.3 | 6 | 30 | 15 | 4.2 | 6 | 24 | 20 | 3.7 | 6 |  |  | -18.3 | Jun
7 | 20 | 14 | -1.3 | 7 | 21 | 17 | 0.7 | 7 | 19 | 14 | -1.8 | 7 | 24 | 19 | 3.2 | 7 | 25 | 21 | 4.7 | 7 |  |  | -18.3 | Jul
8 | 21 | 14 | -0.8 | 8 | 23 | 19 | 2.7 | 8 | 20 | 16 | -0.3 | 8 | 20 | 17 | 0.2 | 8 | 29 | 20 | 6.2 | 8 |  |  | -18.3 | Aug
9 | 22 | 15 | 0.2 | 9 | 21 | 18 | 1.2 | 9 | 23 | 17 | 1.7 | 9 | 20 | 16 | -0.3 | 9 | 28 | 21 | 6.2 | 9 |  |  | -18.3 | Sep
10 | 22 | 15 | 0.2 | 10 | 19 | 14 | -1.8 | 10 | 19 | 13 | -2.3 | 10 | 16 | 14 | -3.3 | 10 | 24 | 20 | 3.7 | 10 |  |  | -18.3 | Oct
11 | 22 | 16 | 0.7 | 11 | 18 | 13 | -2.8 | 11 | 17 | 12 | -3.8 | 11 | 17 | 12 | -3.8 | 11 | 24 | 18 | 2.7 | 11 |  |  | -18.3 | Nov
12 | 24 | 13 | 0.2 | 12 | 18 | 13 | -2.8 | 12 | 18 | 13 | -2.8 | 12 | 16 | 13 | -3.8 | 12 | 25 | 19 | 3.7 | 12 |  |  | -18.3 | Dec | 0 | 0
13 | 18 | 12 | -3.3 | 13 | 19 | 14 | -1.8 | 13 | 18 | 16 | -1.3 | 13 | 18 | 11 | -3.8 | 13 | 24 | 18 | 2.7 | 13 |  |  | -18.3
14 | 17 | 12 | -3.8 | 14 | 18 | 13 | -2.8 | 14 | 19 | 15 | -1.3 | 14 | 20 | 12 | -2.3 | 14 | 24 | 21 | 4.2 | 14 |  |  | -18.3 |  | -328.9 | 207
15 | 19 | 13 | -2.3 | 15 | 18 | 12 | -3.3 | 15 | 19 | 15 | -1.3 | 15 | 24 | 14 | 0.7 | 15 | 25 | 22 | 5.2 | 15 |  |  | -18.3
16 | 15 | 9 | -6.3 | 16 | 11 | 7 | -9.3 | 16 | 19 | 14 | -1.8 | 16 | 26 | 17 | 3.2 | 16 | 24 | 19 | 3.2 | 16 |  |  | -18.3
17 | 15 | 12 | -4.8 | 17 | 13 | 7 | -8.3 | 17 | 20 | 15 | -0.8 | 17 | 27 | 17 | 3.7 | 17 | 25 | 20 | 4.2 | 17 |  |  | -18.3
18 | 14 | 8 | -7.3 | 18 | 13 | 7 | -8.3 | 18 | 20 | 15 | -0.8 | 18 | 32 | 19 | 7.2 | 18 | 32 | 14 | 4.7 | 18 |  |  | -18.3
19 | 17 | 10 | -4.8 | 19 | 14 | 7 | -7.8 | 19 | 19 | 17 | -0.3 | 19 | 33 | 24 | 10.2 | 19 | 26 | 20 | 4.7 | 19 |  |  | -18.3
20 | 17 | 10 | -4.8 | 20 | 19 | 14 | -1.8 | 20 | 21 | 18 | 1.2 | 20 | 22 | 15 | 0.2 | 20 | 26 | 21 | 5.2 | 20 |  |  | -18.3
21 | 16 | 9 | -5.8 | 21 | 18 | 13 | -2.8 | 21 | 23 | 14 | 0.2 | 21 | 21 | 17 | 0.7 | 21 | 25 | 24 | 6.2 | 21 |  |  | -18.3
22 | 17 | 10 | -4.8 | 22 | 21 | 12 | -1.8 | 22 | 26 | 14 | 1.7 | 22 | 21 | 18 | 1.2 | 22 | 26 | 23 | 6.2 | 22 |  |  | -18.3
23 | 18 | 12 | -3.3 | 23 | 19 | 13 | -2.3 | 23 | 33 | 17 | 6.7 | 23 | 20 | 18 | 0.7 | 23 | 25 | 22 | 5.2 | 23 |  |  | -18.3
24 | 17 | 11 | -4.3 | 24 | 19 | 12 | -2.8 | 24 | 15 | 12 | -4.8 | 24 | 24 | 18 | 2.7 | 24 | 26 | 23 | 6.2 | 24 |  |  | -18.3
25 | 21 | 12 | -1.8 | 25 | 18 | 13 | -2.8 | 25 | 15 | 12 | -4.8 | 25 | 23 | 18 | 2.2 | 25 | 27 | 22 | 6.2 | 25 |  |  | -18.3
26 | 18 | 11 | -3.8 | 26 | 18 | 13 | -2.8 | 26 | 16 | 10 | -5.3 | 26 | 22 | 16 | 0.7 | 26 | 26 | 23 | 6.2 | 26 |  |  | -18.3
27 | 14 | 10 | -6.3 | 27 | 18 | 13 | -2.8 | 27 | 17 | 11 | -4.3 | 27 | 22 | 18 | 1.7 | 27 | 25 | 22 | 5.2 | 27 |  |  | -18.3
28 | 14 | 10 | -6.3 | 28 | 17 | 13 | -3.3 | 28 | 17 | 13 | -3.3 | 28 | 26 | 16 | 2.7 | 28 | 0 | 0 | -18.3 | 28 |  |  | -18.3
29 | 16 | 12 | -4.3 |  |  |  |  | 29 | 17 | 14 | -2.8 | 29 | 29 | 18 | 5.2 | 29 | 0 | 0 | -18.3 | 29 |  |  | -18.3
30 | 10 | 4 | -11.3 |  |  |  |  | 30 | 19 | 13 | -2.3 | 30 | 25 | 21 | 4.7 | 30 | 0 | 0 | -18.3 | 30 |  |  | -18.3
31 | 21 | 16 | 0.2 |  |  |  |  | 31 | 18 | 13 | -2.8 |  |  |  |  | 31 | 0 | 0 | -18.3
| Heating degree days | Cooling degree days |  |  | Heating degree days | Cooling degree days |  |  | Heating degree days | Cooling degree days |  |  | Heating degree days | Cooling degree days |  |  | Heating degree days | Cooling degree days |  |  | Heating degree days | Cooling degree days
| -92.6 | 2.8 |  |  | -75.9 | 6.5 |  |  | -64.8 | 11.5 |  |  | -30.3 | 55.3 |  |  | -73.2 | 130.9 |  |  | -512.4 | 0
Jul | Max (A) | Min (B) | (A+B)/2 -18.3=(C) | Aug | Max (A) | Min (B) | (A+B)/2 -18.3=(C) | Sep | Max (A) | Min (B) | (A+B)/2 -18.3=(C) | Oct | Max (A) | Min (B) | (A+B)/2 -18.3=(C) | Nov | Max (A) | Min (B) | (A+B)/2 -18.3=(C) | Dec | Max (A) | Min (B) | (A+B)/2 -18.3=(C)
1 |  |  | -18.3 | 1 |  |  | -18.3 | 1 |  |  | -18.3 | 1 |  |  | -18.3 | 1 |  |  | -18.3 | 1 |  |  | -18.3
2 |  |  | -18.3 | 2 |  |  | -18.3 | 2 |  |  | -18.3 | 2 |  |  | -18.3 | 2 |  |  | -18.3 | 2 |  |  | -18.3
3 |  |  | -18.3 | 3 |  |  | -18.3 | 3 |  |  | -18.3 | 3 |  |  | -18.3 | 3 |  |  | -18.3 | 3 |  |  | -18.3
4 |  |  | -18.3 | 4 |  |  | -18.3 | 4 |  |  | -18.3 | 4 |  |  | -18.3 | 4 |  |  | -18.3 | 4 |  |  | -18.3
5 |  |  | -18.3 | 5 |  |  | -18.3 | 5 |  |  | -18.3 | 5 |  |  | -18.3 | 5 |  |  | -18.3 | 5 |  |  | -18.3
6 |  |  | -18.3 | 6 |  |  | -18.3 | 6 |  |  | -18.3 | 6 |  |  | -18.3 | 6 |  |  | -18.3 | 6 |  |  | -18.3
7 |  |  | -18.3 | 7 |  |  | -18.3 | 7 |  |  | -18.3 | 7 |  |  | -18.3 | 7 |  |  | -18.3 | 7 |  |  | -18.3
8 |  |  | -18.3 | 8 |  |  | -18.3 | 8 |  |  | -18.3 | 8 |  |  | -18.3 | 8 |  |  | -18.3 | 8 |  |  | -18.3
9 |  |  | -18.3 | 9 |  |  | -18.3 | 9 |  |  | -18.3 | 9 |  |  | -18.3 | 9 |  |  | -18.3 | 9 |  |  | -18.3
10 |  |  | -18.3 | 10 |  |  | -18.3 | 10 |  |  | -18.3 | 10 |  |  | -18.3 | 10 |  |  | -18.3 | 10 |  |  | -18.3
11 |  |  | -18.3 | 11 |  |  | -18.3 | 11 |  |  | -18.3 | 11 |  |  | -18.3 | 11 |  |  | -18.3 | 11 |  |  | -18.3
12 |  |  | -18.3 | 12 |  |  | -18.3 | 12 |  |  | -18.3 | 12 |  |  | -18.3 | 12 |  |  | -18.3 | 12 |  |  | -18.3
13 |  |  | -18.3 | 13 |  |  | -18.3 | 13 |  |  | -18.3 | 13 |  |  | -18.3 | 13 |  |  | -18.3 | 13 |  |  | -18.3
14 |  |  | -18.3 | 14 |  |  | -18.3 | 14 |  |  | -18.3 | 14 |  |  | -18.3 | 14 |  |  | -18.3 | 14 |  |  | -18.3
15 |  |  | -18.3 | 15 |  |  | -18.3 | 15 |  |  | -18.3 | 15 |  |  | -18.3 | 15 |  |  | -18.3 | 15 |  |  | -18.3
16 |  |  | -18.3 | 16 |  |  | -18.3 | 16 |  |  | -18.3 | 16 |  |  | -18.3 | 16 |  |  | -18.3 | 16 |  |  | -18.3
17 |  |  | -18.3 | 17 |  |  | -18.3 | 17 |  |  | -18.3 | 17 |  |  | -18.3 | 17 |  |  | -18.3 | 17 |  |  | -18.3
18 |  |  | -18.3 | 18 |  |  | -18.3 | 18 |  |  | -18.3 | 18 |  |  | -18.3 | 18 |  |  | -18.3 | 18 |  |  | -18.3
19 |  |  | -18.3 | 19 |  |  | -18.3 | 19 |  |  | -18.3 | 19 |  |  | -18.3 | 19 |  |  | -18.3 | 19 |  |  | -18.3
20 |  |  | -18.3 | 20 |  |  | -18.3 | 20 |  |  | -18.3 | 20 |  |  | -18.3 | 20 |  |  | -18.3 | 20 |  |  | -18.3
21 |  |  | -18.3 | 21 |  |  | -18.3 | 21 |  |  | -18.3 | 21 |  |  | -18.3 | 21 |  |  | -18.3 | 21 |  |  | -18.3
22 |  |  | -18.3 | 22 |  |  | -18.3 | 22 |  |  | -18.3 | 22 |  |  | -18.3 | 22 |  |  | -18.3 | 22 |  |  | -18.3
23 |  |  | -18.3 | 23 |  |  | -18.3 | 23 |  |  | -18.3 | 23 |  |  | -18.3 | 23 |  |  | -18.3 | 23 |  |  | -18.3
24 |  |  | -18.3 | 24 |  |  | -18.3 | 24 |  |  | -18.3 | 24 |  |  | -18.3 | 24 |  |  | -18.3 | 24 |  |  | -18.3
25 |  |  | -18.3 | 25 |  |  | -18.3 | 25 |  |  | -18.3 | 25 |  |  | -18.3 | 25 |  |  | -18.3 | 25 |  |  | -18.3
26 |  |  | -18.3 | 26 |  |  | -18.3 | 26 |  |  | -18.3 | 26 |  |  | -18.3 | 26 |  |  | -18.3 | 26 |  |  | -18.3
27 |  |  | -18.3 | 27 |  |  | -18.3 | 27 |  |  | -18.3 | 27 |  |  | -18.3 | 27 |  |  | -18.3 | 27 |  |  | -18.3
28 |  |  | -18.3 | 28 |  |  | -18.3 | 28 |  |  | -18.3 | 28 |  |  | -18.3 | 28 |  |  | -18.3 | 28 |  |  | -18.3
29 |  |  | -18.3 | 29 |  |  | -18.3 | 29 |  |  | -18.3 | 29 |  |  | -18.3 | 29 |  |  | -18.3 | 29 |  |  | -18.3
30 |  |  | -18.3 | 30 |  |  | -18.3 | 30 |  |  | -18.3 | 30 |  |  | -18.3 | 30 |  |  | -18.3 | 30 |  |  | -18.3
31 |  |  | -18.3 | 31 |  |  | -18.3 |  |  |  |  | 31 |  |  | -18.3 |  |  |  |  | 31 |  |  | -18.3
| Heating degree days | Cooling degree days |  |  | Heating degree days | Cooling degree days |  |  | Heating degree days | Cooling degree days |  |  | Heating degree days | Cooling degree days |  |  | Heating degree days | Cooling degree days |  |  | Heating degree days | Cooling degree days
| -567.3 | 0 |  |  | -567.3 | 0 |  |  | -549 | 0 |  |  | -567.3 | 0 |  |  | -549 | 0 |  |  | -567.3 | 0
[13 empty] | Heating degree days | Cooling degree days
ANNUAL DEGREE DAYS
[8 empty] | Accurate when inputting is complete |  |  |  |  | -4216.4 | 207
http://www.accuweather.com/en/lb/beirut
Note on A7: Insert property name

## Utility Cost
Utility Expense
2021-05-04
|  | Rate | 1507.5 |  | 27 | 31
Utility | Qt | Cost | Total LLP | Total per day | MTD | Estimation MTD | Forecast MTD | Budget
Water Truck | 0 | 1.66 | 0 | 0 | 0 | 0 | 0 | 0
City Water | 1660 | 8200 | 12361500 | 264.5161 | 7141.9355 | 8200 | 8200 | 8200
Diesel | 38273.8 | 0.982 | 56659193.937 | 1392.0323 | 37584.8716 | 37584.8716 | 18139 | 18139
Gas | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
Electricity | 44321 |  | 12628925 | 310.2739 | 8377.3964 | 9618.4921 | 19000 | 19000
|  |  |  | 1966.8223 | 53104.2034 | 55403.3637 | 45339 | 45339
| MTD | Last Year MTD | Budget MTD | Diff MTD /last Y MDT | Diff MTD /Budget
Cooling Deg | 130.9 | 25.3 |  | 105.6 | 0 |  | 10064.3637 | 10064.3637
Heating Deg | -73.2 | -54.6 |  | -18.6 | 0
Av temp deg C | 23.1481 | 22.5161 |  | 0.63202 | 0
Occ % | 0% | 1.93% | 0% | -1.93% | 0%
Generator RH | 274 | 119.49 | 172.7389 | 154.51 | 101.2611
RH/DAY | 10.1481 | 3.8545

## MDB
ATS-4 | descriptions | STATUS | Sensors | indicator | Trip/switching | location | Load | Date
MDB-3 | NW 20 H1 |  |  |  |  | Main Distribution Board -3
DP-MCP | NS400A |  |  |  |  | Mechanical panel B1
MCC-5B-2 | NS1000N |  |  |  |  | Mechanical B5
CHILLER-3 | NS1000N |  |  |  |  | CHILLER-3
MCC-5-B1 | NS1000N |  |  |  |  | Mechanical B5
ATS-5 | descriptions | STATUS | sensors | indicator | Trip/switching
EMDB-2 | NW 20 H1 |  |  |  |  | Emergency Main Distribution Board -2
EDP-1F | NS630B |  |  |  |  | Power panel 1st floor
EDP-1B | NS630B |  |  |  |  | Power panel 1st Basement
EDP-2F | NS630B |  |  |  |  | Power panel 2nnd floor
EDP-R-LIFTS | NS800 |  |  |  |  | Power panel 1st floor
LVBUSBAR -2 | NW 20 H1 |  |  |  |  | Bus bar
ATS-3 | Descriptions | Status | Sensor | indicator | Trip/switching
EMDB-1 | NW 20 H1 |  |  |  |  | Emergency Main Distribution Board -1
EDP-GF | 400 |  |  |  |  | Electrical Panel GF
EDP-5B | 400 |  |  |  |  | Electrical Panel B5
EDP-LAN | 400 |  |  |  |  | Electrical Panel laundry
EDP-TF1 | 400 |  |  |  |  | Electrical Panel lower technical
EDP-1B-LIFTS | 400 |  |  |  |  | Lift B1
EDP-14 | 800 |  |  |  |  | EP 14th floor
LV BUSBAR 1 | NW 20 H1 |  |  |  |  | Bus bar
ATS-2 | Descriptions | Status | Sensor | indicator | Trip/switching
MDB-2 | NW 20 H1 |  |  |  |  | Main Distribution Board -3
EMCP-CT | 400 | M |  |  |  | Cooling Tower
EMCP-TF1 | 400 | M |  |  |  | Mechanical panel lower technical
MCC-5B-3 | 400 |  |  |  |  | Mechanical panel B5
CHILLER-2 | 1000 |  |  |  |  | CHILLER-2
Geothermal | 1000
ATS1 | Descriptions | Status | Sensor | indicator | Trip/switching
MDB1 | NW 20 H1 |  |  |  |  | Main Distribution Board -3
DP-2F | 1000 |  |  |  |  | Electrical 2nd floor
DP-1B | 630 |  |  |  |  | Electrical B1
DP-1F | 630 |  |  |  |  | Electrical F1
DP-GF | 630 |  |  |  |  | Electrical GF
DP-LAN | 400 |  |  |  |  | Electrical Panel laundry
CHILLER-1 | 1000 |  |  |  |  | CHILLER-1