## TOTAL
Site Name | Day | Month | Year | Total Electricity Kwh | Electricity Tariff ($/Kwh) | Natual Gas (m3) | Natural Gas $/m3 | Water Utility Supply (m3) m3 | Water Utility Supply (m3) $/m3 | Room Nights | Total Guests | Utilities day cost dh
Mumbai | 1 | 5 | 2021 | 15988 | 9 | 334 | 50 | 136 | 100 | 86 | 140 | #REF!
Mumbai | 2 | 5 | 2021 | 15961 | 9 | 445 | 50 | 111 | 100 | 59 | 83 | #REF!
Mumbai | 3 | 5 | 2021 | 16029 | 9 | 438 | 50 | 116 | 100 | 53 | 49 | #REF!
Mumbai | 4 | 5 | 2021 | 16163 | 9 | 584 | 50 | 107 | 100 | 62 | 81 | #REF!
Mumbai | 5 | 5 | 2021 | 15754 | 9 | 287 | 50 | 113 | 100 | 48 | 64 | #REF!
Mumbai | 6 | 5 | 2021 | 15577 | 9 | 477 | 50 | 56 | 100 | 47 | 41 | #REF!
Mumbai | 7 | 5 | 2021 | 14931 | 9 | 348 | 50 | 56 | 100 | 57 | 71 | #REF!
Mumbai | 8 | 5 | 2021 | 19453 | 9 | 613.48 | 50 | 115 | 100 | 83 | 282 | #REF!
Mumbai | 9 | 5 | 2021 | 15329 | 9 | 523.52 | 50 | 95 | 100 | 56 | 189 | #REF!
Mumbai | 10 | 5 | 2021 | 15144 | 9 | 243 | 50 | 77 | 100 | 50 | 72 | #REF!
Mumbai | 11 | 5 | 2021 | 14482.59 | 9 | 333.69 | 50 | 75 | 100 | 52 | 52 | #REF!
Mumbai | 12 | 5 | 2021 | 15169.28 | 9 | 436.43 | 50 | 52 | 100 | 54 | 45 | #REF!
Mumbai | 13 | 5 | 2021 | 14565.96 | 9 | 650.88 | 50 | 77 | 100 | 49 | 60 | #REF!
Mumbai | 14 | 5 | 2021 | 14303.68 | 9 | 292.58 | 50 | 77 | 100 | 66 | 77 | #REF!
Mumbai | 15 | 5 | 2021 | 17032.49 | 9 | 437.42 | 50 | 116 | 100 | 107 | 173 | #REF!
Mumbai | 16 | 5 | 2021 | 15022 | 9 | 317 | 50 | 117 | 100 | 74 | 115 | #REF!
Mumbai | 17 | 5 | 2021 | 14872 | 9 | 562 | 50 | 76 | 100 | 67 | 75 | #REF!
Mumbai | 18 | 5 | 2021 | 15342 | 9 | 400 | 50 | 105 | 100 | 53 | 64 | #REF!
Mumbai | 19 | 5 | 2021 | 14419 | 9 | 248 | 50 | 60 | 100 | 56 | 77 | #REF!
Mumbai | 20 | 5 | 2021 | 15123 | 9 | 288 | 50 | 57 | 100 | 73 | 102 | #REF!
Mumbai | 21 | 5 | 2021 | 16012 | 9 | 534 | 50 | 96 | 100 | 87 | 127 | #REF!
Mumbai | 22 | 5 | 2021 | 17759 | 9 | 632 | 50 | 150 | 100 | 124 | 272 | #REF!
Mumbai | 23 | 5 | 2021 | 16907.05 | 9 | 366.935 | 50 | 140 | 100 | 87 | 217 | #REF!
Mumbai | 24 | 5 | 2021 | 16547.62 | 9 | 510.695 | 50 | 110 | 100 | 59 | 90 | #REF!
Mumbai | 25 | 5 | 2021 | 16235.4 | 9 | 675.289 | 50 | 120 | 100 | 62 | 84 | #REF!
Mumbai | 26 | 5 | 2021 | 19224.56 | 9 | 374.081 | 50 | 113 | 100 | 88 | 419 | #REF!
Mumbai | 27 | 5 | 2021 | 16772.37 | 9 | 615 | 50 | 121 | 100 | 72 | 106 | #REF!
Mumbai | 28 | 5 | 2021 | 16848 | 9 | 458 | 50 | 100 | 100 | 91 | 163 | #REF!
Mumbai | 29 | 5 | 2021 | 16913 | 9 | 318 | 50 | 117 | 100 | 137 | 245 | #REF!
Mumbai | 30 | 5 | 2021 | 17872 | 9 | 484 | 50 | 138 | 100 | 76 | 180 | #REF!
Mumbai | 31 | 5 | 2021 | 17744 | 10 | 640 | 50 | 121 | 100 | 69 | 95

## Submetering
Site Name | Day | Month | Year | HVAC | Fire & Emergency PP | Main PP | Lighting PP | CH-1+ CH2+CH3+CH4 | Chilled water Pump | Ball Room-1 | Ball Room-2 | MK-1 | MK-2 | Prato | San- Qi Indian | San- Qi Japanese | The club | AER | COLD ROOM'S | Ball Room 1 | Ball Room 2 | B1 Laundry | B2 Laundry | STP | MOCK Up Room | 27th Floor | Physic57 | Pinoor Legal- Power+lighting | 2nd floor plant room | 5th Floor | 5th Floor | 12th Floor | 20th Floor | 27th Floor | 34th Floor | Sanqi | Cooling Tower | R.o.plant | STP Water Prod | Domestic Zone-1 | Domestic Zone-2 | Domestic Zone-3 | Flush Zone -1 | Flush Zone -2 | Flush Zone -3 | Swimming pool | B2 Laundry | Boiler Feed Water | cooling tower filling water | STP flush(new water meter) | Garden Water Pump | Flush Zone 2 pump meter | Flush Zone 3 Pump Meter (wtp transfer ) | Flush Tanker-Zone-1 | Total Domestic Water (Tanker (R.O) +BMC) | Total Domestic Consumption | Total STP Consumption | MGL | HWG | Prato | BR-1 | SanQi IND | SanQi JPN | Boiler
Mumbai | 1 | 5 | 2021 | 2167.87 | 1282 | 1352 | 2595 | 4654.53 | 2319 | 949 | 634.8 | 17 | 2 | 30 | 54 | 57 | 50 | 124 | 189 | 394 | 81 | 12 | 0 | 255 | 51 | 10 | 28 | 7 | 0 | 4 | 211 | 208 | 271 | 222 | 0 | 82 | 715 | 52 | 95 | 72 | 12 | 17 | 5 | 9 | 5 | 0 | 0 | 0 | 85 | 0 | 27 | 9 | 5 | 5 | 136 | 115 | 117 | 334 | 232.54 | 0 | 59.56 | 0 | 0.3 | 41.6
Mumbai | 2 | 5 | 2021 | 2008.13 | 1264 | 1301 | 2441 | 5001 | 2231 | 884 | 644.26 | 15 | 1 | 16 | 52 | 56 | 47 | 95 | 177 | 380 | 66 | 14 | 113 | 241 | 21 | 6 | 24 | 6 | 0 | 4 | 208 | 199 | 272 | 214 | 0 | 93 | 712 | 36 | 101 | 42 | 12 | 18 | 5 | 4 | 4 | 0 | 8 | 3 | 40 | 0 | 0 | 4 | 4 | 5 | 111 | 80 | 45 | 445 | 203 | 0 | 73 | 0 | 0 | 169
Mumbai | 3 | 5 | 2021 | 2173.87 | 1224 | 1342 | 2337 | 4821 | 2220 | 1056 | 662.69 | 15 | 1 | 15 | 54 | 54 | 50 | 101 | 174 | 359 | 68 | 25 | 91 | 249 | 184 | 10 | 146 | 6 | 0 | 3 | 213 | 198 | 265 | 185 | 0 | 85 | 818 | 52 | 111 | 62 | 17 | 15 | 4 | 6 | 4 | 0 | 0 | 3 | 41 | 0 | 22 | 6 | 4 | 4 | 116 | 103 | 67 | 438 | 197 | 0 | 58 | 0 | 0 | 183.4
Mumbai | 4 | 5 | 2021 | 2161 | 1213 | 1255 | 2251 | 5147 | 2199 | 1029 | 860.89 | 17 | 1 | 11 | 11 | 54 | 51 | 55 | 188 | 362 | 75 | 12 | 218 | 179 | 243 | 12 | 30 | 7 | 0 | 4 | 206 | 202 | 266 | 151 | 0 | 78 | 816 | 52 | 111 | 31 | 9 | 18 | 6 | 5 | 4 | 0 | 11 | 9 | 60 | 10 | 0 | 5 | 4 | 6 | 107 | 98 | 66 | 584 | 189 | 0 | 45 | 0 | 0 | 350
Mumbai | 5 | 5 | 2021 | 2118 | 1190 | 1208 | 2239 | 4970 | 2244 | 990 | 693.11 | 15 | 1 | 22 | 50 | 49 | 47 | 46 | 177 | 339 | 70 | 10 | 43 | 189 | 198 | 18 | 23 | 6 | 0 | 4 | 205 | 200 | 250 | 147 | 0 | 70 | 782 | 26 | 69 | 31 | 6 | 11 | 7 | 3 | 20 | 4 | 0 | 3 | 39 | 22 | 24 | 3 | 20 | 7 | 113 | 71 | 70 | 287 | 202 | 0 | 51 | 0 | 0 | 34
Mumbai | 6 | 5 | 2021 | 2168 | 1189 | 1199 | 2160 | 4851 | 2297 | 848 | 613.85 | 31 | 1 | 15 | 54 | 52 | 50 | 49 | 157 | 351 | 123 | 41 | 123 | 214 | 29 | 18 | 23 | 6 | 0 | 4 | 204 | 175 | 252 | 145 | 0 | 41 | 830 | 0 | 100 | 39 | 9 | 9 | 8 | 3 | 3 | 4 | 0 | 3 | 40 | 0 | 0 | 3 | 3 | 8 | 56 | 63 | 48 | 477 | 206 | 0 | 57 | 0 | 0 | 214
Mumbai | 7 | 5 | 2021 | 2063 | 1225 | 1112 | 2122 | 4616 | 2190 | 857 | 538.96 | 2 | 1 | 12 | 55 | 55 | 50 | 72 | 144 | 367 | 31 | 19 | 0 | 197 | 32 | 28 | 24 | 7 | 0 | 4 | 207 | 170 | 249 | 125 | 0 | 34 | 846 | 0 | 71 | 31 | 8 | 10 | 5 | 5 | 9 | 5 | 6 | 1 | 59 | 0 | 19 | 5 | 9 | 5 | 56 | 63 | 83 | 348 | 204 | 0 | 71 | 0 | 0 | 73
Mumbai | 8 | 5 | 2021 | 2427.6 | 1346.89 | 1203.34 | 2445.82 | 4895.38 | 2425.27 | 1386.31 | 599.72 | 15 | 1 | 11.7 | 66.63 | 54.92 | 48 | 69 | 104 | 373.72 | 71.8 | 11.66 | 205.13 | 156 | 28.72 | 1.7 | 20.95 | 7.3 | 0 | 3.54 | 207.59 | 208.2 | 277.49 | 166.27 | 0 | 141.4 | 794 | 53 | 49 | 78 | 9 | 13 | 14 | 4 | 4 | 0 | 6 | 8 | 41 | 12 | 0 | 4 | 4 | 14 | 115 | 108 | 55 | 613.48 | 209.84 | 0.4 | 77.5 | 0.2 | 0.6 | 324.94
Mumbai | 9 | 5 | 2021 | 2125.53 | 1183.98 | 1229.73 | 2303.18 | 4766.73 | 2140.73 | 861.69 | 726.74 | 16 | 1 | 10.3 | 51.37 | 55.08 | 48 | 66 | 106 | 389.28 | 76.2 | 33.34 | 11.87 | 232 | 30.28 | 10.3 | 22.05 | 6.1 | 0 | 3.46 | 195.41 | 186.8 | 253.51 | 170.73 | 0 | 112.6 | 798 | 32 | 106 | 40 | 11 | 15 | 10 | 5 | 4 | 0 | 157 | 184 | 50 | 9 | 0 | 5 | 4 | 10 | 95 | 75 | 60 | 523.52 | 186.16 | 0 | 62.5 | 0 | 0.4 | 274.46
Mumbai | 10 | 5 | 2021 | 1851 | 1187 | 1067 | 2173 | 4860.89 | 2128 | 939 | 558.2 | 17 | 1 | 12 | 53 | 57 | 52 | 70 | 109 | 343 | 77 | 11 | 49 | 162 | 93 | 17 | 119 | 17 | 0 | 4 | 203 | 134 | 259 | 126 | 0 | 100 | 636 | 0 | 45 | 24 | 7 | 9 | 12 | 6 | 2 | 8 | 0 | 1 | 40 | 11 | 6 | 6 | 2 | 12 | 77 | 48 | 58 | 243 | 200 | 0 | 35 | 0 | 0 | 8
Mumbai | 11 | 5 | 2021 | 1869.23 | 1191.5 | 998.37 | 2053.4 | 4824.34 | 2093.19 | 771.95 | 528.53 | 14 | 1 | 11.75 | 50.74 | 55.05 | 46 | 64 | 142 | 328.92 | 76 | 10 | 0.25 | 124 | 31 | 15 | 22 | 15 | 0 | 3.8 | 207.77 | 129.13 | 244.79 | 117.95 | 0 | 39.61 | 552 | 0 | 44 | 26 | 8 | 10 | 6 | 3 | 1 | 0 | 0 | 0 | 53 | 0 | 12 | 3 | 1 | 6 | 75 | 48 | 71 | 333.69 | 203 | 0 | 60.8 | 0 | 0 | 69.89
Mumbai | 12 | 5 | 2021 | 1863.44 | 1184.36 | 1220.27 | 2176.72 | 5003 | 2094.11 | 814.4 | 549 | 9 | 1 | 9.98 | 50.73 | 51.41 | 49 | 65 | 112 | 315.12 | 74.96 | 37.52 | 97.71 | 222 | 30.84 | 11 | 81.91 | 11.5 | 0 | 3.78 | 221.58 | 176.35 | 247.69 | 118.6 | 0 | 43.21 | 552 | 20 | 119 | 35 | 6 | 9 | 27 | 6 | 4 | 0 | 0 | 5 | 48 | 25 | 0 | 6 | 4 | 27 | 52 | 60 | 75 | 436.43 | 200.9 | 0 | 51.66 | 0 | 0 | 184.27
Mumbai | 13 | 5 | 2021 | 1794.56 | 1166.14 | 1148.22 | 2066.62 | 4621.1 | 2011.33 | 820.8 | 592 | 11 | 1 | 8.81 | 51.16 | 51.12 | 38 | 76 | 120 | 319.96 | 70.04 | 10.48 | 248.16 | 169 | 71.16 | 10 | 20.72 | 10 | 0.18 | 3.78 | 205.94 | 150.04 | 244.45 | 125.06 | 0 | 43.45 | 551 | 30 | 67 | 52 | 6 | 12 | 27 | 8 | 4 | 0 | 15 | 5 | 60 | 30 | 14 | 8 | 4 | 27 | 77 | 82 | 101 | 650.88 | 204.88 | 0 | 52.63 | 0 | 0 | 393.57
Mumbai | 14 | 5 | 2021 | 1788.72 | 1194.91 | 1089.11 | 2207.44 | 4497.89 | 2007.9 | 785.84 | 573 | 10 | 1 | 8.62 | 50.96 | 53.99 | 23 | 146 | 122 | 353.32 | 80.84 | 12.05 | 0.15 | 176 | 23.4 | 7.8 | 51.37 | 7.8 | 0 | 3.79 | 206.76 | 165.65 | 252.61 | 213.98 | 0 | 42.8 | 562 | 15 | 83 | 46 | 10 | 17 | 26 | 6 | 4 | 0 | 0 | 0 | 40 | 17 | 0 | 6 | 4 | 26 | 77 | 83 | 66 | 292.58 | 201.31 | 0 | 48.91 | 0 | 0 | 42.36
Mumbai | 15 | 5 | 2021 | 2006.92 | 1297.09 | 1315.96 | 2647.82 | 5855.14 | 2074.8 | 895.01 | 595 | 10 | 1 | 6.84 | 52.41 | 57.43 | 25 | 144 | 125 | 373.68 | 75.16 | 37.95 | 36.73 | 252 | 80.6 | 7.2 | 4 | 7.2 | 0.18 | 2.85 | 201.95 | 270.83 | 271.46 | 339.41 | 0 | 89.93 | 599 | 153 | 131 | 42 | 10 | 33 | 23 | 7 | 1 | 0 | 0 | 3 | 42 | 30 | 17 | 7 | 1 | 23 | 116 | 93 | 82 | 437.42 | 200.91 | 0.4 | 45 | 0 | 0 | 191.11
Mumbai | 16 | 5 | 2021 | 1926.13 | 1239 | 1097 | 2608 | 4448 | 2126 | 821 | 668.82 | 7 | 0 | 9 | 54 | 56 | 29 | 118 | 120 | 333 | 82 | 10 | 0 | 116 | 28 | 4 | 9 | 4 | 0 | 4 | 201 | 295 | 260 | 332 | 0 | 95 | 511 | 45 | 29 | 27 | 12 | 17 | 5 | 9 | 5 | 0 | 0 | 0 | 85 | 0 | 0 | 9 | 5 | 5 | 136 | 115 | 117 | 317 | 209 | 0 | 57 | 0 | 0 | 51
Mumbai | 17 | 5 | 2021 | 1602 | 1338.13 | 1050 | 2646 | 4494 | 2036 | 762 | 615.8 | 6 | 1 | 6 | 59 | 57 | 29 | 89 | 117 | 311 | 76 | 11 | 199 | 175 | 36 | 7 | 66 | 7 | 0 | 4 | 266 | 284 | 272 | 322 | 0 | 87 | 419 | 0 | 93 | 45 | 7 | 6 | 2 | 22 | 8 | 0 | 14 | 6 | 20 | 0 | 0 | 22 | 8 | 2 | 76 | 88 | 22 | 562 | 214 | 0 | 46 | 0 | 0 | 302
Mumbai | 18 | 5 | 2021 | 1530 | 1254 | 1081 | 2625 | 5084.54 | 2115 | 802 | 543.32 | 6 | 2 | 4 | 53 | 56 | 30 | 75 | 128 | 300 | 80 | 26 | 63 | 240 | 31 | 14 | 68 | 14.2 | 0.18 | 4 | 337 | 268 | 270 | 300 | 0 | 78 | 353 | 0 | 146 | 29 | 12 | 8 | 4 | 10 | 0 | 0 | 0 | 2 | 73 | 0 | 4 | 10 | 0 | 4 | 105 | 59 | 81 | 400 | 195 | 0 | 45 | 0 | 0 | 160
Mumbai | 19 | 5 | 2021 | 1650.87 | 1200 | 999 | 2579 | 4451.99 | 2088.67 | 793 | 572.16 | 10 | 1 | 5 | 56 | 58 | 29 | 82 | 123 | 293 | 77 | 11 | 1 | 153 | 23 | 21 | 24 | 21 | 0.02 | 4 | 323 | 210 | 234 | 236 | 0 | 104 | 355 | 0 | 75 | 23 | 7 | 12 | 11 | 7 | 2 | 0 | 0 | 0 | 40 | 11 | 0 | 7 | 2 | 11 | 60 | 51 | 51 | 248 | 173 | 0 | 42 | 0 | 0 | 33
Mumbai | 20 | 5 | 2021 | 1818 | 1255 | 978 | 2517 | 4744 | 2118 | 870 | 538.38 | 9 | 0 | 8 | 52 | 57 | 33 | 50 | 117 | 357 | 76 | 10 | 15 | 94 | 24 | 27 | 23 | 27 | 0 | 4 | 267 | 205 | 256 | 279 | 0 | 67 | 365 | 22 | 34 | 27 | 11 | 16 | 10 | 14 | 3 | 0 | 0 | 0 | 39 | 18 | 0 | 14 | 3 | 10 | 57 | 71 | 49 | 288 | 204 | 0 | 48 | 0 | 0 | 36
Mumbai | 21 | 5 | 2021 | 1843.13 | 1333 | 1150.07 | 2103 | 5144 | 2133 | 800 | 623.18 | 10 | 2 | 6 | 53 | 55 | 34 | 184 | 136 | 331 | 79 | 26 | 133 | 145 | 21 | 22 | 25 | 22 | 0 | 3 | 175 | 206 | 261 | 481 | 0 | 76 | 379 | 37 | 83 | 49 | 9 | 20 | 6 | 4 | 7 | 7 | 4 | 5 | 39 | 3 | 0 | 4 | 7 | 6 | 96 | 89 | 45 | 534 | 194 | 0 | 67 | 0 | 0 | 273
Mumbai | 22 | 5 | 2021 | 1920 | 1372 | 1280 | 3496 | 6030 | 2210 | 918 | 600 | 10 | 1 | 8 | 54 | 56 | 42 | 197 | 129 | 377 | 76 | 11 | 244 | 174 | 88 | 13 | 23 | 13.8 | 0 | 4 | 209 | 203 | 311 | 522 | 0 | 106 | 451 | 63 | 101 | 80 | 9 | 25 | 13 | 10 | 17 | 4 | 13 | 4 | 40 | 26 | 14 | 10 | 17 | 13 | 150 | 141 | 67 | 632 | 194 | 0 | 64 | 0 | 0 | 374
Mumbai | 23 | 5 | 2021 | 2173.43 | 1310.38 | 1286.43 | 2942.66 | 5435.9 | 2171.6 | 854.15 | 607.26 | 10 | 0 | 6.65 | 58.12 | 54.3 | 38 | 127 | 131 | 357.64 | 79.56 | 11.07 | 29.15 | 211 | 22.56 | 6.3 | 23.73 | 6.4 | 0 | 3.87 | 204.74 | 208.1 | 312.42 | 495.17 | 0 | 192.1 | 556 | 57 | 92 | 37 | 15 | 31 | 21 | 5 | 11 | 0 | 0 | 2 | 60 | 19 | 0 | 5 | 11 | 21 | 140 | 99 | 81 | 366.935 | 214.84 | 0 | 60.84 | 0.2 | 0 | 91.455
Mumbai | 24 | 5 | 2021 | 2126.48 | 1287.37 | 1238.28 | 2764.88 | 5182.04 | 2226.2 | 864.44 | 578.92 | 9 | 2 | 7.03 | 58.09 | 57.53 | 42 | 92 | 123 | 342.4 | 80.48 | 30.08 | 98.22 | 135 | 25.28 | 18 | 125.3 | 18 | 0 | 3.85 | 214.25 | 219.75 | 302.76 | 430.23 | 0 | 85.28 | 653 | 28 | 74 | 40 | 11 | 16 | 28 | 5 | 7 | 0 | 1 | 3 | 40 | 40 | 0 | 5 | 7 | 28 | 110 | 79 | 68 | 510.695 | 230.16 | 0 | 71.79 | 0 | 0 | 208.745
Mumbai | 25 | 5 | 2021 | 2110.88 | 1247.85 | 1212.33 | 2568.6 | 5004.34 | 2198.7 | 860.52 | 844.16 | 9 | 14 | 6.11 | 54.4 | 57.02 | 46 | 101 | 121 | 365.08 | 89.12 | 10.59 | 244.14 | 183 | 24 | 33.4 | 23.93 | 33.4 | 0 | 3.75 | 198.07 | 259.15 | 252.61 | 362.61 | 0 | 71.59 | 649 | 54 | 97 | 78 | 9 | 13 | 7 | 8 | 12 | 0 | 16 | 0 | 50 | 0 | 16 | 8 | 12 | 7 | 120 | 120 | 73 | 675.289 | 208.4 | 0 | 74.12 | 0 | 0 | 392.769
Mumbai | 26 | 5 | 2021 | 2644.96 | 1344 | 1226.35 | 2690.88 | 5995.25 | 2602.8 | 1413.72 | 613.9 | 13 | 17 | 7.28 | 68.89 | 53.15 | 41 | 9 | 132 | 383.92 | 78.56 | 10.68 | 37.17 | 190 | 30.48 | 18.8 | 22.05 | 18.8 | 0 | 3.63 | 174.64 | 185.88 | 245.63 | 385.56 | 0 | 139.54 | 786 | 38 | 79 | 43 | 9 | 18 | 5 | 5 | 6 | 0 | 1 | 7 | 98 | 24 | 0 | 5 | 6 | 5 | 113 | 81 | 103 | 374.081 | 207.51 | 0 | 71.22 | 0 | 0 | 95.351
Mumbai | 27 | 5 | 2021 | 2481.25 | 1296.4 | 1176.54 | 2773.98 | 4767.47 | 2345.7 | 845.17 | 766.84 | 10 | 1 | 5.93 | 59.5 | 54 | 44 | 64 | 112 | 342.96 | 80.28 | 24.58 | 82.32 | 167 | 34.68 | 17.5 | 21.99 | 17.9 | 0 | 2.9 | 196.3 | 214.12 | 267.58 | 446.43 | 0 | 100.49 | 763 | 35 | 86 | 49 | 11 | 18 | 4 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 205.09 | 0 | 53.03 | 0 | 0 | 356.88
Mumbai | 28 | 5 | 2021 | 2485 | 1279 | 1195.07 | 2711 | 4796 | 2329.33 | 832 | 600.26 | 14 | 1 | 7 | 58 | 57 | 39 | 110 | 134 | 345 | 77 | 11 | 213 | 149 | 34 | 18 | 23 | 18 | 0 | 4 | 191 | 218 | 248 | 372 | 0 | 126 | 879 | 28 | 80 | 51 | 7 | 18 | 4 | 6 | 4 | 0 | 14 | 5 | 56 | 0 | 0 | 6 | 4 | 4 | 100 | 86 | 60 | 458 | 197 | 0 | 66 | 0 | 0.4 | 194.8
Mumbai | 29 | 5 | 2021 | 2408 | 1353.87 | 1218 | 2918 | 4832 | 2325.67 | 866 | 525.64 | 11 | 1 | 7 | 56 | 58 | 38 | 195 | 138 | 392 | 86 | 11 | 0 | 169 | 35 | 15 | 23 | 15 | 0 | 4 | 193 | 213 | 281 | 539 | 0 | 89 | 872 | 39 | 68 | 46 | 9 | 35 | 4 | 7 | 6 | 0 | 0 | 0 | 66 | 18 | 17 | 7 | 6 | 4 | 117 | 103 | 87 | 318 | 197 | 0 | 66 | 0 | 0 | 55.4
Mumbai | 30 | 5 | 2021 | 2377 | 1302.13 | 1330.93 | 2954 | 5573 | 2307 | 926 | 572.66 | 14 | 1 | 6 | 54 | 55 | 41 | 194 | 161 | 381 | 98 | 23 | 91 | 224 | 36 | 12 | 24 | 12 | 0 | 4 | 192 | 216 | 301 | 526 | 0 | 138 | 802 | 0 | 112 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 484 | 217 | 0.4 | 65 | 0 | 0 | 201.6
Mumbai | 31 | 5 | 2021 | 2344.87 | 1260 | 1249 | 2684 | 5603 | 2277 | 884 | 528.2 | 12 | 1 | 7 | 54 | 56 | 48 | 78 | 158 | 359 | 89 | 12 | 270 | 193 | 23 | 94 | 10.6 | 94 | 0 | 0 | 187 | 221 | 283 | 422 | 0 | 104 | 805 | 110 | 79 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 177 | 0 | 58 | 2 | 1 | 402

## Daily HLP
Date | Date | Min.Tem (Degee) | Avg.Temp (Degree) | Hum % | Occu. | KWAH |  | Electricity |  |  |  | Gas |  |  | Water |  |  | Water per occiped room | Diesel |  |  | Water Consumption Zone |  |  |  | Chiller Running Hrs |  |  |  |  | Chiller Total | Chiller Avg. Laod | Boiler Running Hrs |  |  | Total boiler | Hot Water Generator |  |  | Total HWG RH | HWG Gas consumption | Transformer -1 | [9 empty] | Transformer -2 | [13 empty] | Total HLP Cost |  | Chiller lock at 70%
[5 empty] | % |  | KVAH | Units (Kwh) | Rate | Total Cost(Rs) | Per room | Total Units(CuM) | Rate | Total Cost(Rs) | Units(KL) | Rate | Total Cost(Rs) |  | Ltrs | Rate | Total Cost(Rs) | Zone-1 | Zone-2 | Zone-3 |  | CH1 | CH2 | CH3 | CH4 | Total chiller |  |  | Boiler1 | Boiler2 | Boiler3 |  | HWG1 | HWG2 |  |  |  | HVAC-1 | FPP-1 | MPP | Lighting-1 | Cap bank 1100KVAR-1 | CH-1 | CH-2 | Chilled water Pump | Co Generator | Ball Room-2 | HVAC-2 | FPP-2 | MPP | Lighting-2 | Cap bank 1200KVAR-2 | CH-3 | CH-4 | Chilled water Pump | Ball Room-1 |  | Cooling Tower consumption | HVAC% | Lighting% | Power% |  | Chiller Plant IKW
1 | 1 |  | 30 | 80% | 84% | 16053 | 16053 | 15988 | 9 | 144477 | 79.1485 | 334 | 35 | 11690 | 136 | 134 | 18224 | 80.1509 | 0 | 69 | 0 | 72 | 12 | 17 | 101 | 23.85 | 0 | 0 | 0 | 23.85 | 4654.53 | 195.1585 | 0 | 0 | 0 | 0 | 8.88 | 0 |  | 8.88 | 232.54 | 2168 | 1282 | 1352 | 1924 | 0 | 4655 | 0 | 2319 | 0 | 391 | -0.13 | 0 | 0 | 671 | 74 | 0 | -0.47 | 0 | 949 | 4654.53 | 715 | 57.1766 | 16.2309 | 8.456% | 174391 | 7688.53 | 1.1513 | 0.4879
2 | 2 |  | 30 | 80% | 60% | 16031 | 16031 | 15961 | 10 | 160310 | 79.0149 | 445 | 35 | 15575 | 111 | 134 | 14874 | 91.5842 | 0 | 69 | 0 | 42 | 12 | 18 | 72 | 23.98 | 0 | 0 | 0 | 23.98 | 5001 | 208.5488 | 2.71 | 0 | 0 | 2.71 | 7.81 | 0 |  | 7.81 | 203 | 2008 | 1264 | 1301 | 1888 | 0 | 5001 | 0 | 2231 | 0 | 385 | 0.13 | 0 | 0 | 553 | 74 | 0 | 0 | 0 | 884 | 5001 | 712 | 57.8919 | 15.2935 | 8.151% | 190759 | 7944 | 1.1831
3 | 3 |  | 29 | 78% | 57% | 16089 | 16089 | 16029 | 10 | 160890 | 79.3515 | 438 | 35 | 15330 | 116 | 134 | 15544 | 100.7469 | 0 | 69 | 0 | 61 | 17 | 15 | 93 | 24 | 0 | 0 | 0 | 24 | 4821 | 200.875 | 0 | 0.4 | 9.01 | 9.41 | 7.4 | 0 |  | 7.4 | 197 | 2174 | 1224 | 1342 | 1807 | 0 | 4821 | 0 | 2220 | 0 | 366 | -0.13 | 0 | 0 | 530 | 74 | 0 | 0 | 0 | 1056 | 4821 | 818 | 57.4887 | 14.5798 | 8.372% | 191764 | 7859 | 1.1695
4 | 4 |  | 34 | 84% | 10% | 16226 | 16226 | 16163 | 10 | 162260 | 80.0149 | 584 | 35 | 20440 | 107 | 134 | 14338 | 529.703 | 0 | 69 | 0 | 62 | 9 | 18 | 89 | 23.69 | 0 | 0 | 0 | 23.69 | 5147 | 217.2647 | 7.21 | -0.4 | 0 | 6.81 | 7.13 | 0 |  | 7.13 | 189 | 2161 | 1213 | 1255 | 1745 | -0.23 | 5099 | 0 | 2199 | 0 | 345 | 0 | 0 | 0 | 506 | 72 | 0 | 48 | 0 | 1029 | 5147 | 818 | 58.8195 | 13.9269 | 7.765% | 197038 | 8164 | 1.2308
5 | 5 |  | 34 | 84% | 11% | 15811 | 15811 | 15754 | 10 | 158110 | 77.9901 | 287 | 35 | 10045 | 113 | 134 | 15142 | 508.5509 | 0 | 69 | 0 | 31 | 6 | 11 | 48 | 24 | 0 | 0 | 0 | 24 | 4970 | 207.0833 | 0 | 0 | 0 | 0 | 7.74 | 0 |  | 7.74 | 202 | 2118 | 1190 | 1208 | 1710 | 0 | 4961 | 0 | 2244 | 0 | 340 | 0 | 0 | 0 | 529 | 71 | 0 | 9 | 0 | 990 | 4970 | 782 | 59.2357 | 14.2123 | 7.668% | 183297 | 7996 | 1.1899
6 | 6 |  | 34 | 84% | 10% | 15655 | 15655 | 15577 | 10 | 156550 | 77.1139 | 477 | 35 | 16695 | 56 | 134 | 7504 | 277.2277 | 0 | 69 | 0 | 39 | 9 | 9 | 57 | 24 | 0 | 0 | -0.44 | 23.56 | 4851 | 205.8998 | 0 | 0 | 11.38 | 11.38 | 7.66 | 0 |  | 7.66 | 206 | 2168 | 1189 | 1199 | 1647 | 0 | 4841 | 0 | 2297 | 0 | 320 | 0 | 0 | 0 | 513 | 74 | 0 | 10 | 0 | 848 | 4851 | 830 | 59.8061 | 13.8666 | 7.697% | 180749 | 7978 | 1.2094
7 | 7 |  | 33 | 80% | 16% | 15022 | 15022 | 14931 | 10 | 150220 | 73.9158 | 348 | 35 | 12180 | 56 | 134 | 7504 | 173.2673 | 0 | 69 | 0 | 31 | 8 | 10 | 49 | 23.6 | 0 | 0 | 0 | 23.6 | 4616 | 195.5932 | 0 | 0 | 0 | 0 | 7.77 | 0 |  | 7.77 | 204 | 2063 | 1225 | 1112 | 1602 | 0 | 4606 | 0 | 2190 | 0 | 310 | 0 | 0 | 0 | 520 | 72 | 0 | 10 | 0 | 857 | 4616 | 846 | 59.3999 | 14.212 | 7.448% | 169904 | 7652 | 1.158
8 | 8 |  | 27 | 78% | 24% | 19564 | 19564 | 19453 | 10 | 195640 | 96.302 | 613.48 | 35 | 21471.8 | 115 | 134 | 15410 | 237.2112 | 0 | 69 | 0 | 78 | 9 | 13 | 100 | 23.65 | 0 | 8.33 | 0 | 31.98 | 4895.38 | 153.0763 | 5.75 | 0 | 1.94 | 7.69 | 7.99 | -0.12 |  | 7.87 | 209.84 | 2427.47 | 1347.02 | 1203.27 | 1924.75 | 0.23 | 4885.19 | 0.08 | 2425.27 | 0 | 0 | 0.13 | -0.13 | 0.07 | 521.07 | 3760.7 | 0 | 10.11 | 0 | 1386.31 | 4895.38 | 794 | 50.1118 | 12.573 | 6.186% | 232521.8 | 8114.65 | 0.90622
9 | 9 |  | 29 | 78% | 60% | 15397 | 15397 | 15329 | 10 | 153970 | 75.8861 | 523.52 | 35 | 18323.2 | 95 | 134 | 12730 | 78.3828 | 0 | 69 | 0 | 40 | 11 | 15 | 66 | 23.08 | 0 | 0 | 0 | 23.08 | 4766.73 | 206.5308 | 3.74 | -0.33 | 3.62 | 7.03 | 6.74 | 0 |  | 6.74 | 186.16 | 2125.53 | 1183.98 | 1229.73 | 1790.25 | 0 | 4766.81 | -0.08 | 2140.73 | 0 | 0 | 0 | 0 | 0 | 512.93 | 71.3 | 0 | 0 | 0 | 861.69 | 4766.73 | 794 | 58.9275 | 15.025 | 8.022% | 185023.2 | 7701.46 | 1.1917
10 | 10 |  | 30 | 78% | 52% | 15255 | 15255 | 15144 | 10 | 152550 | 74.9703 | 243 | 35 | 8505 | 77 | 134 | 10318 | 73.3054 | 0 | 69 | 0 | 24 | 7 | 9 | 40 | 24.03 | 0 | 0 | 0 | 24.03 | 4860.89 | 202.2842 | 0 | 0 | 0.13 | 0.13 | 7.58 | 0 |  | 7.58 | 200 | 1851 | 1187 | 1067 | 1650 | 0 | 4861 | 0 | 2128 | 0 | 0 | 0 | 0 | 0 | 523 | 73 | 0 | -0.11 | 0 | 939 | 4860.89 | 794 | 58.3722 | 14.3489 | 7.046% | 171373 | 7782.89 | 1.1567
11 | 11 |  | 29 | 80% | 50% | 14613.82 | 14613.82 | 14482.59 | 10 | 146138.2 | 71.696 | 333.69 | 35 | 11679.15 | 75 | 134 | 10050 | 74.2574 | 0 | 69 | 0 | 26 | 8 | 10 | 44 | 24.04 | 0 | -0.33 | 0 | 23.71 | 4824.34 | 203.4728 | 0 | 0.463 | 0 | 0.463 | 7.67 | 0 |  | 7.67 | 203 | 1869.23 | 1191.5 | 998.37 | 1567.17 | 86.24 | 4794.03 | 0.08 | 2093.19 | 0 | 0 | 0 | 0 | 0 | 486.23 | 72.65 | 0 | 30.23 | 0 | 771.95 | 4824.34 | 552 | 60.6712 | 14.1784 | 6.894% | 167867.35 | 7469.53 | 1.1251
12 | 12 |  | 30 | 78% | 50% | 15259.89 | 15259.89 | 15169.28 | 10 | 152598.9 | 75.0954 | 436.43 | 35 | 15275.05 | 52 | 134 | 6968 | 51.4851 | 0 | 69 | 0 | 35 | 6 | 9 | 50 | 20.95 | 0 | 3.43 | 0 | 24.38 | 5003 | 205.2092 | 0 | -0.003 | 10.05 | 10.047 | 7.52 | 0 |  | 7.52 | 200.9 | 1863.44 | 1184.36 | 1220.27 | 1670.24 | 64.27 | 4377.52 | 0 | 2094.11 | 0 | 0 | 0 | 0 | 0 | 506.48 | 73.4 | 615.96 | 9.52 | 0 | 814.4 | 5003 | 552 | 59.0704 | 14.3495 | 8.044% | 174841.95 | 7649.11 | 1.1205
13 | 13 |  | 29 | 78% | 50% | 14671.02 | 14671.02 | 14565.96 | 10 | 146710.2 | 72.1087 | 650.88 | 35 | 22780.8 | 77 | 134 | 10318 | 76.2376 | 0 | 69 | 0 | 52 | 6 | 12 | 70 | 0 | 0 | 24.47 | 0 | 24.47 | 4621.1 | 188.8476 | 7.92 | 0 | 0 | 7.92 | 7.56 | 0 |  | 7.56 | 204.88 | 1794.56 | 1166.14 | 1148.22 | 1649.18 | 59.29 | 0 | 0 | 2011 | 0 | 0 | 0 | 0 | 0 | 417.44 | 75.16 | 4611.14 | 9.96 | 0.33 | 820.8 | 4621.1 | 551 | 57.854 | 14.188 | 7.883% | 179809 | 7183.43 | 1.0484
14 | 14 |  | 30 | 78% | 63% | 14430.55 | 14430.55 | 14303.68 | 10 | 144305.5 | 70.8103 | 292.58 | 35 | 10240.3 | 77 | 134 | 10318 | 60.5061 | 0 | 69 | 0 | 46 | 10 | 17 | 73 | 0 | 0 | 24.23 | 0.42 | 24.65 | 4497.89 | 182.4702 | 0 | 0 | 0 | 0 | 7.58 | 0 |  | 7.58 | 201.31 | 1788.72 | 1194.91 | 1089.11 | 1783.3 | 53 | 0 | 0 | 2007.9 | 0 | 0 | 0 | 0 | 0 | 424.14 | 71.8 | 4497.89 | 0 | 0 | 785.84 | 4497.89 | 562 | 57.9886 | 15.4327 | 7.614% | 164863.8 | 7067.79 | 1.024
15 | 15 |  | 31 | 78% | 83% | 17116.72 | 17116.72 | 17032.49 | 10 | 171167.2 | 84.3193 | 437.42 | 35 | 15309.7 | 116 | 134 | 15544 | 69.1876 | 0 | 69 | 0 | 42 | 10 | 33 | 85 | 2.17 | 0 | 23.93 | 0 | 26.1 | 5855.14 | 224.3349 | 0 | 0 | 9.53 | 9.53 | 7.62 | 0 |  | 7.62 | 200.91 | 2007.05 | 1297.09 | 1316.03 | 2173.11 | 34.97 | 471.45 | -0.08 | 2074.8 | 0 | 0 | -0.13 | 0 | -0.07 | 474.71 | 70.99 | 5373.01 | 10.76 | 0 | 895.01 | 5855.14 | 599 | 58.3406 | 15.5457 | 7.726% | 202020.9 | 8528.94 | 1.1671
16 | 16 |  | 30 | 78% | 52% | 15155 | 15155 | 15022 | 10 | 151550 | 74.3663 | 317 | 35 | 11095 | 117 | 134 | 15678 | 111.3861 | 0 | 69 | 0 | 27 | 14 | 19 | 60 | 0 | 0 | 23.59 | 0 | 23.59 | 4448 | 188.5545 | 0 | 0 | 0 | 0 | 7.97 | 0 |  | 7.97 | 209 | 1926 | 1239 | 1097 | 2154 | 52 | 0 | 0 | 2126 | 0 | 0 | 0.13 | 0 | 0 | 454 | 73 | 4448 | 0 | 0 | 821 | 4448 | 511 | 56.5845 | 17.3612 | 7.303% | 178323 | 7085 | 1.0726
17 | 17 |  | 29 | 80% | 60% | 15048 | 15048 | 14872 | 10 | 150480 | 73.6238 | 562 | 35 | 19670 | 76 | 134 | 10184 | 62.7063 | 0 | 69 | 0 | 45 | 7 | 6 | 58 | 0 | 0 | 24.45 | 0 | 24.45 | 4494 | 183.8037 | 6.28 | 0 | 0 | 6.28 | 8.05 | 0 |  | 8.05 | 214 | 1602 | 1338 | 1050 | 2155 | 80 | 0 | 0 | 2036 | 0 | 0 | 0 | 0.13 | 0 | 491 | 80 | 4494 | 0 | 0 | 762 | 4494 | 419 | 54.6799 | 17.7918 | 7.06% | 180334 | 6949 | 1.015
18 | 18 |  | 29 | 79% | 54% | 15496 | 15496 | 15342 | 10 | 154960 | 75.9505 | 400 | 35 | 14000 | 105 | 134 | 14070 | 96.2596 | 0 | 69 | 0 | 29 | 12 | 8 | 49 | 0 | 0 | 23.9 | 0 | 23.9 | 5084.54 | 212.7423 | 0 | 0 | 8.53 | 8.53 | 7.74 | 0 |  | 7.74 | 195 | 1530 | 1254 | 1081 | 2101 | 89 | 0 | 0 | 2115 | 0 | 0 | 0 | 0 | 0 | 524 | 78 | 5084.54 | 0 | 0 | 802 | 5084.54 | 353 | 56.8996 | 17.1099 | 7.046% | 183030 | 7552.54 | 1.1286
19 | 19 |  | 27 | 84% | 10% | 14549 | 14549 | 14419 | 10 | 145490 | 71.3812 | 248 | 35 | 8680 | 60 | 134 | 8040 | 297.0297 | 0 | 69 | 0 | 23 | 7 | 12 | 42 | 0 | 0 | 24 | -0.06 | 23.94 | 4451.99 | 185.9645 | 0 | 0 | 0.02 | 0.02 | 7.3 | 0 |  | 7.3 | 173 | 1651 | 1200 | 999 | 2013 | 68 | 0 | 0 | 2089 | 0 | 0 | -0.13 | 0 | 0 | 566 | 82 | 4403.46 | 48.53 | -0.33 | 793 | 4451.99 | 355 | 56.8107 | 17.8861 | 6.928% | 162210 | 6895.66 | 1.0287
20 | 20 |  | 27 | 84% | 24% | 15231 | 15231 | 15123 | 10 | 152310 | 74.8663 | 288 | 35 | 10080 | 57 | 134 | 7638 | 117.5743 | 0 | 69 | 0 | 27 | 11 | 16 | 54 | 0 | 0 | 24 | 0 | 24 | 4744 | 197.6667 | 0 | 0 | 0 | 0 | 8.19 | 0 |  | 8.19 | 204 | 1818 | 1255 | 978 | 1961 | 0 | 0 | 0 | 2118 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 4734 | 10 | 0 | 870 | 4744 | 365 | 57.396 | 12.967 | 6.467% | 170028 | 7227 | 1.0754
21 | 21 |  | 21 | 84% | 24% | 16096 | 16096 | 16012 | 10 | 160960 | 79.2673 | 534 | 35 | 18690 | 96 | 134 | 12864 | 198.0198 | 0 | 69 | 0 | 49 | 9 | 20 | 78 | 0 | 0 | 24 | 0 | 24 | 5144 | 214.3333 | 2.71 | 0 | 6.63 | 9.34 | 7.02 | 0 |  | 7.02 | 194 | 1843 | 1333 | 1150 | 1537 | 0 | 0 | 0 | 2133 | 0 | 0 | 0.13 | 0 | 0.07 | 566 | 82 | 5134 | 10 | 0 | 800 | 5144 | 379 | 56.9581 | 13.1339 | 7.183% | 192514 | 7656 | 1.1393
22 | 22 |  | 27 | 84% | 35% | 17814 | 17814 | 17759 | 10 | 178140 | 87.9158 | 632 | 35 | 22120 | 150 | 134 | 20100 | 212.1641 | 0 | 69 | 0 | 80 | 9 | 25 | 114 | 3.58 | 0 | 24 | 0.01 | 27.59 | 6030 | 218.5574 | 7.54 | 0 | 0 | 7.54 | 7.36 | 0 |  | 7.36 | 194 | 1920 | 1372 | 1280 | 2952 | 99 | 810 | 0 | 2210 | 0 | 0 | 0 | 0 | 0 | 544 | 80 | 5210 | 10 | 0 | 918 | 6030 | 451 | 57.2104 | 19.6858 | 7.208% | 220360 | 8691 | 1.125
23 | 23 |  | 30 | 78% | 52% | 16981.75 | 16981.75 | 16907.05 | 10 | 169817.5 | 83.6983 | 366.935 | 35 | 12842.725 | 140 | 134 | 18760 | 133.2826 | 0 | 69 | 0 | 37 | 15 | 31 | 83 | 0 | 0 | 24.39 | 0 | 24.39 | 5435.9 | 222.8741 | 0 | 0 | 2.45 | 2.45 | 8.05 | 0 |  | 8.05 | 214.84 | 2173.43 | 1310.51 | 1286.43 | 2431.55 | 0.48 | 0.13 | -1.03 | 2171.6 | 0 | 0 | 0 | -0.13 | 0 | 511.11 | 80.96 | 5426.61 | 10.19 | 0 | 854.15 | 5435.9 | 556 | 57.8512 | 17.4049 | 7.609% | 201420.225 | 8163.5 | 1.1954
24 | 24 |  | 28 | 80% | 63% | 16604.88 | 16604.88 | 16547.62 | 10 | 166048.8 | 81.9189 | 510.695 | 35 | 17874.325 | 110 | 134 | 14740 | 86.4372 | 0 | 69 | 0 | 40 | 11 | 16 | 67 | 24 | 0 | 0 | 0 | 24 | 5182.04 | 215.9183 | 0 | 0 | 10.25 | 10.25 | 8.52 | -0.3 |  | 8.22 | 230.16 | 2126.48 | 1287.37 | 1238.28 | 2245.96 | 0 | 0 | 0 | 2226.2 | 0 | 0 | 0 | 0 | 0 | 518.92 | 81.95 | 5172.12 | 9.92 | 0 | 864.44 | 5182.04 | 653 | 57.6199 | 16.7086 | 7.483% | 198663.125 | 8061.24 | 1.1996
25 | 25 |  | 31 | 80% | 54% | 16299.04 | 16299.04 | 16235.4 | 10 | 162990.4 | 80.3733 | 675.289 | 35 | 23635.115 | 120 | 134 | 16080 | 110.011 | 0 | 69 | 0 | 78 | 9 | 13 | 100 | 0 | 0 | 23.91 | 0 | 23.91 | 5004.34 | 209.299 | 0 | 0 | 10.25 | 10.25 | 8.05 | -0.3 |  | 7.75 | 208.4 | 2110.88 | 1247.85 | 1212.33 | 2043.76 | 0 | 0 |  | 2198.7 | 0 | 0 | 0 | 0 | 0 | 524.84 | 81.95 | 4994.74 | 9.6 | 0 | 860.52 | 5004.34 | 649 | 57.368 | 15.821 | 7.467% | 202705.515 | 7852.04 | 1.1729
26 | 26 |  | 28 | 74% | 54% | 19361.72 | 19361.72 | 19224.56 | 10 | 193617.2 | 95.1711 | 374.081 | 35 | 13092.835 | 113 | 134 | 15142 | 103.5937 | 0 | 69 | 0 | 43 | 9 | 18 | 70 | 0 | 0 | 24.04 | 12.07 | 36.11 | 5995.25 | 166.0274 | 0.01 | -0.01 | 2.83 | 2.83 | 7.78 | 0 |  | 7.78 | 207.51 | 2644.96 | 1344 | 1226.35 | 2149.2 | 202.51 | 0 | 0 | 2602.8 | 0 | 0 | 0 | 0 | 0 | 541.68 | 83.38 | 3911.21 | 2084.04 | 0 | 1413.72 | 5995.25 | 786 | 58.4825 | 13.9971 | 6.379% | 221852.035 | 9384.05 | 0.92812
27 | 27 |  | 30 | 78% | 70% | 16839.61 | 16839.61 | 16772.37 | 10 | 168396.1 | 83.0315 | 615 | 35 | 21525 | 121 | 134 | 16214 | 85.5728 | 0 | 69 | 0 | 49 | 11 | 17 | 77 | 0 | 0 | 0 | 24.04 | 24.04 | 4767.47 | 198.3141 | 0 | 0 | 9.78 | 9.78 | 7.63 | 0 |  | 7.63 | 205.09 | 2481.25 | 1296.27 | 1176.61 | 2221.53 | 0.01 | -0.13 | 0.03 | 2345.7 | 0 | 0 | 0 | 0.13 | -0.07 | 552.45 | 81 | 0.32 | 4767.25 | 0 | 845.17 | 4767.47 | 763 | 57.2037 | 16.539 | 7.015% | 206135.1 | 7876.17 | 1.1701
28 | 28 |  | 30 | 78% | 71% | 16930 | 16930 | 16848 | 10 | 169300 | 83.4059 | 458 | 35 | 16030 | 100 | 134 | 13400 | 69.7253 | 0 | 69 | 0 | 51 | 7 | 18 | 76 | -0.1 | 0 | -0.34 | 24.12 | 23.68 | 4796 | 202.5338 | 7.64 | 0.1 | 0.04 | 7.78 | 7.19 | 0 |  | 7.19 | 197 | 2485 | 1279 | 1195 | 2110 | 0 | 0 | 0 | 2329 | 0 | 0 | 0 | 0 | 0.07 | 601 | 82 | 0 | 4796 | 0.33 | 832 | 4796 | 879 | 57.0414 | 16.0909 | 7.093% | 198730 | 8004.33 | 1.2072
29 | 29 |  | 30 | 78% | 98% | 16984 | 16984 | 16913 | 10 | 169840 | 83.7277 | 318 | 35 | 11130 | 117 | 134 | 15678 | 59.1028 | 0 | 69 | 0 | 46 | 9 | 35 | 90 | 0 | 0 | 0 | 24.08 | 24.08 | 4832 | 200.6645 | 0 | 0.18 | 0 | 0.18 | 7.44 | 0.12 |  | 7.56 | 197 | 2408 | 1354 | 1218 | 2330 | 0 | 0 | 0 | 2326 | 0 | 0 | 0 | -0.13 | 0 | 588 | 80 | 0 | 4832 | -0.33 | 866 | 4832 | 872 | 56.5581 | 17.253 | 7.202% | 196648 | 8029.67 | 1.1909
30 | 30 |  | 29 | 80% | 62% | 17940 | 17940 | 17872 | 10 | 179400 | 88.4752 | 484 | 35 | 16940 | 138 | 134 | 18492 | 110.1884 | 0 | 69 | 0 | 38 | 13 | 34 | 85 | 0 | 0 | 0 | 24.03 | 24.03 | 5573 | 231.9184 | 0 | -0.18 | 9.74 | 9.56 | 8.09 | 0 |  | 8.09 | 217 | 2377 | 1302 | 1331 | 2409 | 0 | 0 | 0 | 2307 | 0 | 0 | 0 | 0.13 | -0.07 | 545 | 82 | 0 | 5573 | 0 | 926 | 5573 | 802 | 57.3915 | 16.5286 | 7.447% | 214832 | 8682 | 1.2904
31 | 31 |  | 30 | Unit | 2900% | 17744 | 17744 | 17744 | 11 | 195184 | 87.8416 | 640 | 36 | 23040 | 121 | 134 | 16214 | 2.0656 | 0 | 70 | 0 | 13 | 34 | 2 | 49 | 0 | 0 | 24.03 | 0 | 24.03 | 5603 | 233.1669 | -0.18 | 9.74 | 8.09 | 17.65 | 0 | 0 |  | 0 | 0.4 | 2345 | 1260 | 1249 | 2175 | 0 | 0 | 1 | 2277 | 0 | 173 | -0.13 | 0 | 0 | 509 | 72 | 0 | 5602 | 0 | 884 | 5603 | 805 | 57.6244 | 15.1262 | 7.039% | 234438 | 8685 | 1.2908
Total |  |  | 29.5161 |  | 140.7% | 502269 | 502269 | 499496 | 310 | 5024381 | 2472.7525 | 13867 | 1086 | 485985 | 3120 | 4154 | 418080 | 4336.9235 | 0 | 2140 | 0 | 1356 | 327 | 506 | 2189 | 312.52 | 0 | 348.03 | 108.27 | 768.82 | 154970.53 | 6278.9881 | 51.33 | 9.96 | 114.27 | 175.56 | 231.03 | -0.6 | 0 | 230.43 | 6100.94 | 64029 | 39011 | 36809 | 61520 | 888.77 | 58950 | 0 | 68286 | 0 | 2630 | -0.13 | 0 | 0 | 15725 | 6063.24 | 68111 | 27909.53 | 0 | 28000 | 154970.53 | 20317 | 1784.8348 | 479.3684 | 2.289 | 5928446 | 243573.53 | 1.1315
| 1 | 0 | 1 | 0 | 0.2 |  |  | 2728.81 | 0 | 26861.7 | 13.509 | 144.84 | 0 | 5069.4 | 39 | 0 | 5226 | 8.6816 | 0 | 0 | 0 | -4 | 0 | 16 | 12 | 2.17 | 0 | -0.3 | -0.42 | 1.45 | 1357.25 | 41.8647 | 0 | 0 | 9.53 | 9.53 | 0.04 | 0 | 0 | 0.04 |  | 218.33 | 102.18 | 226.92 | 389.81 | -18.03 | 471.45 | -0.08 | 66.9 |  |  | -0.13 | 0 | -0.07 | 50.57 | -0.81 | 875.12 | 10.76 | 0 |  |  |  | 0.35197 | 0.11303 |  | 37157.1 | 1461.15
[5 empty] | 1.4074 |  |  | 31218.5
| Guest complaint |  |  |  | 140.7%
14.1875

## Occupancy
| Hotel Occupancy Occ% | Room Nights | Comp Night | Cummulative % | Total Covers Guests | Total Room Nights
1 |  | 62 | 24 | 42.5743 | 140 | 86
2 |  | 35 | 24 | 29.2079 | 83 | 59
3 |  | 30 | 23 | 26.2376 | 49 | 53
4 |  | 37 | 25 | 30.6931 | 81 | 62
5 |  | 24 | 24 | 23.7624 | 64 | 48
6 |  | 22 | 25 | 23.2673 | 41 | 47
7 |  | 32 | 25 | 28.2178 | 71 | 57
8 |  | 57 | 26 | 41.0891 | 282 | 83
9 |  | 29 | 27 | 27.7228 | 189 | 56
10 |  | 23 | 27 | 24.7525 | 72 | 50
11 |  | 25 | 27 | 25.7426 | 52 | 52
12 |  | 27 | 27 | 26.7327 | 45 | 54
13 |  | 22 | 27 | 24.2574 | 60 | 49
14 |  | 39 | 27 | 32.6733 | 77 | 66
15 |  | 79 | 28 | 52.9703 | 173 | 107
16 |  | 37 | 37 | 36.6337 | 115 | 74
17 |  | 38 | 29 | 33.1683 | 75 | 67
18 |  | 28 | 25 | 26.2376 | 64 | 53
19 |  | 32 | 24 | 27.7228 | 77 | 56
20 |  | 49 | 24 | 36.1386 | 102 | 73
21 |  | 62 | 25 | 43.0693 | 127 | 87
22 |  | 98 | 26 | 61.3861 | 272 | 124
23 |  | 61 | 26 | 43.0693 | 217 | 87
24 |  | 33 | 26 | 29.2079 | 90 | 59
25 |  | 36 | 26 | 30.6931 | 84 | 62
26 |  | 60 | 28 | 43.5644 | 419 | 88
27 |  | 44 | 28 | 35.6436 | 106 | 72
28 |  | 64 | 27 | 45.0495 | 163 | 91
29 |  | 110 | 27 | 67.8218 | 245 | 137
30 |  | 49 | 27 | 37.6238 | 180 | 76
31 |  | 42 | 27 | 34.1584 | 95 | 69
| Total |  |  |  | 3910 | 2204

## Water Report
| Date | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
| occupancy | 50% | 10% | 50%
| Tanker | 80 | 60 | 60 | 60 | 60 | 0 | 0 | 60 | 40 | 20 | 20 | 0 | 20 | 20 | 60 | 60 | 20 | 0 | 0 | 0 | 40 | 90 | 80 | 50 | 60 | 60 | 60 | 40 | 60 | 80 | 60
| BMC | 56 | 51 | 56 | 47 | 53 | 56 | 56 | 55 | 55 | 57 | 55 | 52 | 57 | 57 | 56 | 57 | 56 | 105 | 60 | 57 | 56 | 60 | 60 | 60 | 60 | 53 | 61 | 60 | 57 | 58 | 61
| R.O. Plant Production | 52 | 36 | 52 | 39 | 26 | 0 | 0 | 53 | 32 | 0 | 0 | 20 | 30 | 15 | 153 | 45 | 0 | 0 | 0 | 22 | 37 | 63 | 57 | 28 | 54 | 38 | 35 | 28 | 39 | 0 | 110
| STP Production | 95 | 101 | 111 | 71 | 69 | 100 | 71 | 49 | 106 | 45 | 44 | 119 | 67 | 83 | 131 | 29 | 93 | 146 | 75 | 34 | 83 | 101 | 92 | 74 | 97 | 79 | 86 | 80 | 68 | 112 | 79
Domestic Water | Zone-1 | 72 | 42 | 61 | 62 | 31 | 39 | 31 | 78 | 40 | 24 | 26 | 35 | 52 | 46 | 42 | 27 | 45 | 29 | 23 | 27 | 49 | 80 | 37 | 40 | 78 | 43 | 49 | 51 | 46 | 38 | 54
| Zone-2 | 12 | 12 | 17 | 9 | 6 | 9 | 8 | 9 | 11 | 7 | 8 | 6 | 6 | 10 | 10 | 14 | 7 | 12 | 7 | 11 | 9 | 9 | 15 | 11 | 9 | 9 | 11 | 7 | 9 | 13 | 12
| Zone-3 | 17 | 18 | 15 | 18 | 11 | 9 | 10 | 13 | 15 | 9 | 10 | 9 | 12 | 17 | 33 | 19 | 6 | 8 | 12 | 16 | 20 | 25 | 31 | 16 | 13 | 18 | 17 | 18 | 35 | 34 | 19
Flushing Water | Zone-1 | 5 | 5 | 4 | 6 | 7 | 8 | 5 | 14 | 10 | 12 | 6 | 27 | 27 | 26 | 23 | 5 | 2 | 4 | 11 | 10 | 6 | 13 | 21 | 28 | 7 | 5 | 8 | 4 | 4 | 2 | 4
| Zone-2 | 9 | 4 | 6 | 5 | 3 | 3 | 5 | 4 | 5 | 6 | 3 | 6 | 8 | 6 | 7 | 28 | 22 | 10 | 7 | 14 | 4 | 10 | 5 | 5 | 8 | 5 | 10 | 6 | 7 | 9 | 8
| Zone-3 | 5 | 4 | 4 | 4 | 20 | 3 | 9 | 4 | 4 | 2 | 1 | 4 | 4 | 4 | 1 | 7 | 8 | 0 | 2 | 3 | 7 | 17 | 11 | 7 | 12 | 6 | 6 | 4 | 6 | 11 | 6
Branches ( Domestic water ) | Pool | 0 | 0 | 0 | 0 | 4 | 4 | 5 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| B2 Laundry | 0 | 8 | 0 | 11 | 0 | 0 | 6 | 6 | 157 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 4 | 13 | 0 | 1 | 16 | 1 | 0 | 14 | 0 | 0 | 15
| Boiler Feed Water | 0 | 3 | 3 | 9 | 3 | 3 | 1 | 8 | 184 | 1 | 0 | 5 | 5 | 0 | 3 | 0 | 6 | 2 | 0 | 0 | 5 | 4 | 2 | 3 | 0 | 7 | 2 | 5 | 0 | 3 | 6
Branches ( STP Water ) | CT water | 85 | 40 | 41 | 60 | 39 | 40 | 59 | 41 | 50 | 40 | 53 | 48 | 60 | 40 | 42 | 107 | 20 | 73 | 40 | 39 | 39 | 40 | 60 | 40 | 50 | 98 | 71 | 56 | 66 | 59 | 64
| STP flush | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 12 | 9 | 11 | 0 | 25 | 30 | 17 | 30 | 0 | 0 | 0 | 11 | 18 | 3 | 26 | 19 | 40 | 0 | 24 | 0 | 0 | 18 | 18 | 0
| Garden | 27 | 0 | 22 | 0 | 24 | 0 | 19 | 0 | 0 | 6 | 12 | 0 | 14 | 0 | 17 | 0 | 0 | 4 | 0 | 0 | 0 | 14 | 0 | 0 | 16 | 0 | 16 | 0 | 17 | 0 | 0
Total Tanke(RO) + BMC |  | 136 | 111 | 116 | 107 | 113 | 56 | 56 | 115 | 95 | 77 | 75 | 52 | 77 | 77 | 116 | 117 | 76 | 105 | 60 | 57 | 96 | 150 | 140 | 110 | 120 | 113 | 121 | 100 | 117 | 138 | 121
Domestic consumption |  | 115 | 80 | 103 | 98 | 71 | 63 | 63 | 108 | 75 | 48 | 48 | 60 | 82 | 83 | 93 | 95 | 88 | 59 | 51 | 71 | 89 | 141 | 99 | 79 | 120 | 81 | 93 | 86 | 103 | 105 | 99 | 0
STP +Flush Consumption |  | 117 | 45 | 67 | 66 | 70 | 48 | 83 | 55 | 60 | 58 | 71 | 75 | 101 | 66 | 82 | 112 | 22 | 81 | 51 | 49 | 45 | 67 | 81 | 68 | 73 | 103 | 95 | 60 | 87 | 61 | 68 | 0
BOH |  | 72 | 42 | 61 | 62 | 31 | 39 | 31 | 78 | 40 | 24 | 26 | 35 | 52 | 46 | 42 | 27 | 45 | 29 | 23 | 27 | 49 | 80 | 37 | 40 | 78 | 43 | 49 | 51 | 46 | 38 | 54
Guest Floor |  | 43 | 38 | 42 | 36 | 40 | 24 | 32 | 30 | 35 | 24 | 22 | 25 | 30 | 37 | 51 | 68 | 43 | 30 | 28 | 44 | 40 | 61 | 62 | 39 | 42 | 38 | 44 | 35 | 57 | 67 | 45
Guest floor% |  | 37.3913 | 47.5 | 40.7767 | 36.7347 | 56.338 | 38.0952 | 50.7937 | 27.7778 | 46.6667 | 50 | 45.8333 | 41.6667 | 36.5854 | 44.5783 | 54.8387 | 71.5789 | 48.8636 | 50.8475 | 54.902 | 61.9718 | 44.9438 | 43.2624 | 62.6263 | 49.3671 | 35 | 46.9136 | 47.3118 | 40.6977 | 55.3398 | 63.8095 | 45.4545

## Section Load
[5 empty] | Transformer -Load | [7 empty] | Electrical | [33 empty] | Boiler Running
[39 empty] | Gas consumption | [6 empty] | Boiler Running Hours
| HT Kwh | HT Kvah | MGL Gas | Water | HVAC | Fire & Emergency PP | Main PP | Lighting PP | CH-1+ CH2+CH3+CH4 | Chilled water Pump | Ball Room-1 | Ball Room-2 | MK-1 | MK-2 | Prato | San- Qi Indian | San- Qi Japanese | The club | AER | COLD ROOM'S | Ball Room 1 | Ball Room 2 | B1 Laundry | B2 Laundry | STP | MOCK Up Room | 27th Floor | Physic57 | Pinoor Legal- Power+lighting | 2nd floor plant room | 5th Floor | 5th Floor | 12th Floor | 20th Floor | 27th Floor | 34th Floor | Sanqi | Cooling Tower | MGL | HWG | Prato | BR-1 | SanQi IND | SanQi JPN | Boiler | HWG | Boiler1 | Boiler2 | Boiler3 (400Kg) | Total
2020-05-01 | 15988 | 16053 | 334 | 136 | 2167.87 | 1282 | 1352 | 2595 | 4654.53 | 2319 | 949 | 634.8 | 17 | 2 | 30 | 54 | 57 | 50 | 124 | 189 | 394 | 81 | 12 | 0 | 255 | 51 | 10 | 28 | 7 | 0 | 4 | 211 | 208 | 271 | 222 | 0 | 82 | 715 | 334 | 232.54 | 0 | 59.56 | 0 | 0.3 | 41.6 | 8.88 | 0 | 0 | 0 | 0
2020-05-02 | 15961 | 16031 | 445 | 111 | 2008.13 | 1264 | 1301 | 2441 | 5001 | 2231 | 884 | 644.26 | 15 | 1 | 16 | 52 | 56 | 47 | 95 | 177 | 380 | 66 | 14 | 113 | 241 | 21 | 6 | 24 | 6 | 0 | 4 | 208 | 199 | 272 | 214 | 0 | 93 | 712 | 445 | 203 | 0 | 73 | 0 | 0 | 169 | 7.81 | 2.71 | 0 | 0 | 2.71
2020-05-03 | 16029 | 16089 | 438 | 116 | 2173.87 | 1224 | 1342 | 2337 | 4821 | 2220 | 1056 | 662.69 | 15 | 1 | 15 | 54 | 54 | 50 | 101 | 174 | 359 | 68 | 25 | 91 | 249 | 184 | 10 | 146 | 6 | 0 | 3 | 213 | 198 | 265 | 185 | 0 | 85 | 818 | 438 | 197 | -0.4 | 58 | 0 | 0 | 183.4 | 7.4 | 0 | 0.4 | 9.01 | 9.41
2020-05-04 | 16163 | 16226 | 584 | 107 | 2161 | 1213 | 1255 | 2251 | 5147 | 2199 | 1029 | 860.89 | 17 | 1 | 11 | 11 | 54 | 51 | 55 | 188 | 362 | 75 | 12 | 218 | 179 | 243 | 12 | 30 | 7 | 0 | 4 | 206 | 202 | 266 | 151 | 0 | 78 | 816 | 584 | 189 | 0 | 45 | 0 | 0 | 350 | 7.13 | 7.21 | -0.4 | 0 | 6.81
2020-05-05 | 15754 | 15811 | 287 | 113 | 2118 | 1190 | 1208 | 2239 | 4970 | 2244 | 990 | 693.11 | 15 | 1 | 22 | 50 | 49 | 47 | 46 | 177 | 339 | 70 | 10 | 43 | 189 | 198 | 18 | 23 | 6 | 0 | 4 | 205 | 200 | 250 | 147 | 0 | 70 | 782 | 287 | 202 | 0 | 51 | 0 | 0 | 34 | 7.74 | 0 | 0 | 0 | 0
2020-05-06 | 15577 | 15655 | 477 | 56 | 2168 | 1189 | 1199 | 2160 | 4851 | 2297 | 848 | 613.85 | 31 | 1 | 15 | 54 | 52 | 50 | 49 | 157 | 351 | 123 | 41 | 123 | 214 | 29 | 18 | 23 | 6 | 0 | 4 | 204 | 175 | 252 | 145 | 0 | 41 | 830 | 477 | 206 | 0 | 57 | 0 | 0 | 214 | 7.66 | 0 | 0 | 11.38 | 11.38
2020-05-07 | 14931 | 15022 | 348 | 56 | 2063 | 1225 | 1112 | 2122 | 4616 | 2190 | 857 | 538.96 | 2 | 1 | 12 | 55 | 55 | 50 | 72 | 144 | 367 | 31 | 19 | 0 | 197 | 32 | 28 | 24 | 7 | 0 | 4 | 207 | 170 | 249 | 125 | 0 | 34 | 846 | 348 | 204 | 0 | 71 | 0 | 0 | 73 | 7.77 | 0 | 0 | 0 | 0
2020-05-08 | 19453 | 19564 | 613.48 | 115 | 2427.6 | 1346.89 | 1203.34 | 2445.82 | 4895.38 | 2425.27 | 1386.31 | 599.72 | 15 | 1 | 11.7 | 66.63 | 54.92 | 48 | 69 | 104 | 373.72 | 71.8 | 11.66 | 205.13 | 156 | 28.72 | 1.7 | 20.95 | 7.3 | 0 | 3.54 | 207.59 | 208.2 | 277.49 | 166.27 | 0 | 141.4 | 794 | 613.48 | 209.84 | 0.4 | 77.5 | 0.2 | 0.6 | 324.94 | 7.87 | 5.75 | 0 | 1.94 | 7.69
2020-05-09 | 15329 | 15397 | 523.52 | 95 | 2125.53 | 1183.98 | 1229.73 | 2303.18 | 4766.73 | 2140.73 | 861.69 | 726.74 | 16 | 1 | 10.3 | 51.37 | 55.08 | 48 | 66 | 106 | 389.28 | 76.2 | 33.34 | 11.87 | 232 | 30.28 | 10.3 | 22.05 | 6.1 | 0 | 3.46 | 195.41 | 186.8 | 253.51 | 170.73 | 0 | 112.6 | 798 | 523.52 | 186.16 | 0 | 62.5 | 0 | 0.4 | 274.46 | 6.74 | 3.74 | -0.33 | 3.62 | 7.03
2020-05-10 | 15144 | 15255 | 243 | 77 | 1851 | 1187 | 1067 | 2173 | 4860.89 | 2128 | 939 | 558.2 | 17 | 1 | 12 | 53 | 57 | 52 | 70 | 109 | 343 | 77 | 11 | 49 | 162 | 93 | 17 | 119 | 17 | 0 | 4 | 203 | 134 | 259 | 126 | 0 | 100 | 636 | 243 | 200 | 0 | 35 | 0 | 0 | 8 | 7.58 | 0 | 0 | 0.13 | 0.13
2020-05-11 | 14482.59 | 14613.82 | 333.69 | 75 | 1869.23 | 1191.5 | 998.37 | 2053.4 | 4824.34 | 2093.19 | 771.95 | 528.53 | 14 | 1 | 11.75 | 50.74 | 55.05 | 46 | 64 | 142 | 328.92 | 76 | 10 | 0.25 | 124 | 31 | 15 | 22 | 15 | 0 | 3.8 | 207.77 | 129.13 | 244.79 | 117.95 | 0 | 39.61 | 552 | 333.69 | 203 | 0 | 60.8 | 0 | 0 | 69.89 | 7.67 | 0 | 0.463 | 0 | 0.463
2020-05-12 | 15169.28 | 15259.89 | 436.43 | 52 | 1863.44 | 1184.36 | 1220.27 | 2176.72 | 5003 | 2094.11 | 814.4 | 549 | 9 | 1 | 9.98 | 50.73 | 51.41 | 49 | 65 | 112 | 315.12 | 74.96 | 37.52 | 97.71 | 222 | 30.84 | 11 | 81.91 | 11.5 | 0 | 3.78 | 221.58 | 176.35 | 247.69 | 118.6 | 0 | 43.21 | 552 | 436.43 | 200.9 | -0.4 | 51.66 | 0 | 0 | 184.27 | 7.52 | 0 | -0.003 | 10.05 | 10.047 | 149.24
2020-05-13 | 14565.96 | 14671.02 | 650.88 | 77 | 1794.56 | 1166.14 | 1148.22 | 2066.62 | 4621.1 | 2011.33 | 820.8 | 592 | 11 | 1 | 8.81 | 51.16 | 51.12 | 38 | 76 | 120 | 319.96 | 70.04 | 10.48 | 248.16 | 169 | 71.16 | 10 | 20.72 | 10 | 0.18 | 3.78 | 205.94 | 150.04 | 244.45 | 125.06 | 0 | 43.45 | 551 | 650.88 | 204.88 | 0 | 52.63 | -0.2 | 0 | 393.57 | 7.56 | 7.92 | 0 | 0 | 7.92 | -188.69
2020-05-14 | 14303.68 | 14430.55 | 292.58 | 77 | 1788.72 | 1194.91 | 1089.11 | 2207.44 | 4497.89 | 2007.9 | 785.84 | 573 | 10 | 1 | 8.62 | 50.96 | 53.99 | 23 | 146 | 122 | 353.32 | 80.84 | 12.05 | 0.15 | 176 | 23.4 | 7.8 | 51.37 | 7.8 | 0 | 3.79 | 206.76 | 165.65 | 252.61 | 213.98 | 0 | 42.8 | 562 | 292.58 | 201.31 | 0 | 48.91 | 0 | 0 | 42.36 | 7.58 | 0 | 0 | 0 | 0 | 158.95
2020-05-15 | 17032.49 | 17116.72 | 437.42 | 116 | 2006.92 | 1297.09 | 1315.96 | 2647.82 | 5855.14 | 2074.8 | 895.01 | 595 | 10 | 1 | 6.84 | 52.41 | 57.43 | 25 | 144 | 125 | 373.68 | 75.16 | 37.95 | 36.73 | 252 | 80.6 | 7.2 | 4 | 7.2 | 0.18 | 2.85 | 201.95 | 270.83 | 271.46 | 339.41 | 0 | 89.93 | 599 | 437.42 | 200.91 | 0.4 | 45 | 0 | 0 | 191.11 | 7.62 | 0 | 0 | 9.53 | 9.53 | 9.8
2020-05-16 | 15022 | 15155 | 317 | 117 | 1926.13 | 1239 | 1097 | 2608 | 4448 | 2126 | 821 | 668.82 | 7 | 0 | 9 | 54 | 56 | 29 | 118 | 120 | 333 | 82 | 10 | 0 | 116 | 28 | 4 | 9 | 4 | 0 | 4 | 201 | 295 | 260 | 332 | 0 | 95 | 511 | 317 | 209 | 0 | 57 | 0 | 0 | 51 | 7.97 | 0 | 0 | 0 | 0 | 158
2020-05-17 | 14872 | 15048 | 562 | 76 | 1602 | 1338.13 | 1050 | 2646 | 4494 | 2036 | 762 | 615.8 | 6 | 1 | 6 | 59 | 57 | 29 | 89 | 117 | 311 | 76 | 11 | 199 | 175 | 36 | 7 | 66 | 7 | -0.18 | 4 | 266 | 284 | 272 | 322 | 0 | 87 | 419 | 562 | 214 | 0 | 46 | 0 | 0 | 302 | 8.05 | 6.28 | 0 | 0 | 6.28 | -88
2020-05-18 | 15342 | 15496 | 400 | 105 | 1530 | 1254 | 1081 | 2625 | 5084.54 | 2115 | 802 | 543.32 | 6 | 2 | 4 | 53 | 56 | 30 | 75 | 128 | 300 | 80 | 26 | 63 | 240 | 31 | 14 | 68 | 14.2 | 0.18 | 4 | 337 | 268 | 270 | 300 | 0 | 78 | 353 | 400 | 195 | 0 | 45 | 0 | 0 | 160 | 7.74 | 0 | 0 | 8.53 | 8.53 | 35
2020-05-19 | 14419 | 14549 | 248 | 60 | 1650.87 | 1200 | 999 | 2579 | 4451.99 | 2088.67 | 793 | 572.16 | 10 | 1 | 5 | 56 | 58 | 29 | 82 | 123 | 293 | 77 | 11 | 1 | 153 | 23 | 21 | 24 | 21 | 0.02 | 4 | 323 | 210 | 234 | 236 | 0 | 104 | 355 | 248 | 173 | 0 | 42 | 0 | 0 | 33 | 7.3 | 0 | 0 | 0.02 | 0.02 | 140
2020-05-20 | 15123 | 15231 | 288 | 57 | 1818 | 1255 | 978 | 2517 | 4744 | 2118 | 870 | 538.38 | 9 | 0 | 8 | 52 | 57 | 33 | 50 | 117 | 357 | 76 | 10 | 15 | 94 | 24 | 27 | 23 | 27 | 0 | 4 | 267 | 205 | 256 | 279 | 0 | 67 | 365 | 288 | 204 | 0 | 48 | 0 | 0 | 36 | 8.19 | 0 | 0 | 0 | 0 | 168
2020-05-21 | 16012 | 16096 | 534 | 96 | 1843.13 | 1333 | 1150.07 | 2103 | 5144 | 2133 | 800 | 623.18 | 10 | 2 | 6 | 53 | 55 | 34 | 184 | 136 | 331 | 79 | 26 | 133 | 145 | 21 | 22 | 25 | 22 | 0 | 3 | 175 | 206 | 261 | 481 | 0 | 76 | 379 | 534 | 194 | 0 | 67 | 0 | 0 | 273 | 7.02 | 2.71 | 0 | 6.63 | 9.34 | -79
2020-05-22 | 17759 | 17814 | 632 | 150 | 1920 | 1372 | 1280 | 3496 | 6030 | 2210 | 918 | 600 | 10 | 1 | 8 | 54 | 56 | 42 | 197 | 129 | 377 | 76 | 11 | 244 | 174 | 88 | 13 | 23 | 13.8 | 0 | 4 | 209 | 203 | 311 | 522 | 0 | 106 | 451 | 632 | 194 | 0 | 64 | 0 | 0 | 374 | 7.36 | 7.54 | 0 | 0 | 7.54 | -180
2020-05-23 | 16907.05 | 16981.75 | 366.935 | 140 | 2173.43 | 1310.38 | 1286.43 | 2942.66 | 5435.9 | 2171.6 | 854.15 | 607.26 | 10 | 0 | 6.65 | 58.12 | 54.3 | 38 | 127 | 131 | 357.64 | 79.56 | 11.07 | 29.15 | 211 | 22.56 | 6.3 | 23.73 | 6.4 | -0.2 | 3.87 | 204.74 | 208.1 | 312.42 | 495.17 | 0 | 192.1 | 556 | 366.935 | 214.84 | 0 | 60.84 | 0.2 | -0.4 | 91.455 | 8.05 | 0 | 0 | 2.45 | 2.45 | 123.385
2020-05-24 | 16547.62 | 16604.88 | 510.695 | 110 | 2126.48 | 1287.37 | 1238.28 | 2764.88 | 5182.04 | 2226.2 | 864.44 | 578.92 | 9 | 2 | 7.03 | 58.09 | 57.53 | 42 | 92 | 123 | 342.4 | 80.48 | 30.08 | 98.22 | 135 | 25.28 | 18 | 125.3 | 18 | 0 | 3.85 | 214.25 | 219.75 | 302.76 | 430.23 | 0 | 85.28 | 653 | 510.695 | 230.16 | 0 | 71.79 | 0 | 0 | 208.745 | 8.22 | 0 | 0 | 10.25 | 10.25 | 21.415
2020-05-25 | 16235.4 | 16299.04 | 675.289 | 120 | 2110.88 | 1247.85 | 1212.33 | 2568.6 | 5004.34 | 2198.7 | 860.52 | 844.16 | 9 | 14 | 6.11 | 54.4 | 57.02 | 46 | 101 | 121 | 365.08 | 89.12 | 10.59 | 244.14 | 183 | 24 | 33.4 | 23.93 | 33.4 | 0 | 3.75 | 198.07 | 259.15 | 252.61 | 362.61 | 0 | 71.59 | 649 | 675.289 | 208.4 | 0 | 74.12 | 0 | 0 | 392.769 | 7.99 | 7.9 | 0.01 | 0 | 7.91 | -184.369
2020-05-26 | 19224.56 | 19361.72 | 374.081 | 113 | 2644.96 | 1344 | 1226.35 | 2690.88 | 5995.25 | 2602.8 | 1413.72 | 613.9 | 13 | 17 | 7.28 | 68.89 | 53.15 | 41 | 9 | 132 | 383.92 | 78.56 | 10.68 | 37.17 | 190 | 30.48 | 18.8 | 22.05 | 18.8 | 0 | 3.63 | 174.64 | 185.88 | 245.63 | 385.56 | 0 | 139.54 | 786 | 374.081 | 207.51 | 0 | 71.22 | 0 | 0 | 95.351 | 7.78 | 0.01 | -0.01 | 2.83 | 2.83 | 112.159
2020-05-27 | 16772.37 | 16839.61 | 615 | 121 | 2481.25 | 1296.4 | 1176.54 | 2773.98 | 4767.47 | 2345.7 | 845.17 | 766.84 | 10 | 1 | 5.93 | 59.5 | 54 | 44 | 64 | 112 | 342.96 | 80.28 | 24.58 | 82.32 | 167 | 34.68 | 17.5 | 21.99 | 17.9 | 0 | 2.9 | 196.3 | 214.12 | 267.58 | 446.43 | 0 | 100.49 | 763 | 615 | 205.09 | 0 | 53.03 | 0 | 0 | 356.88 | 7.63 | 0 | 0 | 9.78 | 9.78 | -151.79
2020-05-28 | 16848 | 16930 | 458 | 100 | 2485 | 1279 | 1195.07 | 2711 | 4796 | 2329.33 | 832 | 600.26 | 14 | 1 | 7 | 58 | 57 | 39 | 110 | 134 | 345 | 77 | 11 | 213 | 149 | 34 | 18 | 23 | 18 | 0 | 4 | 191 | 218 | 248 | 372 | 0 | 126 | 879 | 458 | 197 | 0 | 66 | -0.2 | 0.4 | 194.8 | 7.19 | 7.64 | 0.1 | 0.04 | 7.78 | 2.2
2020-05-29 | 16913 | 16984 | 318 | 117 | 2408 | 1353.87 | 1218 | 2918 | 4832 | 2325.67 | 866 | 525.64 | 11 | 1 | 7 | 56 | 58 | 38 | 195 | 138 | 392 | 86 | 11 | 0 | 169 | 35 | 15 | 23 | 15 | 0 | 4 | 193 | 213 | 281 | 539 | 0 | 89 | 872 | 318 | 197 | -0.4 | 66 | 0 | 0 | 55.4 | 7.56 | 0 | 0.18 | 0 | 0.18 | 141.6
2020-05-30 | 17872 | 17940 | 484 | 138 | 2377 | 1302.13 | 1330.93 | 2954 | 5573 | 2307 | 926 | 572.66 | 14 | 1 | 6 | 54 | 55 | 41 | 194 | 161 | 381 | 98 | 23 | 91 | 224 | 36 | 12 | 24 | 12 | 0 | 4 | 192 | 216 | 301 | 526 | 0 | 138 | 802 | 484 | 217 | 0.4 | 65 | 0 | 0 | 201.6 | 8.09 | 0 | -0.18 | 9.74 | 9.56 | 15.4
2020-05-31 | 17683 | 17744 | 640 | 121 | 2344.87 | 1260 | 1249 | 2684 | 5603 | 2277 | 884 | 528.2 | 12 | 1 | 7 | 54 | 56 | 48 | 78 | 158 | 359 | 89 | 12 | 270 | 193 | 23 | 94 | 10.6 | 94 | 0 | 0 | 187 | 221 | 283 | 422 | 0 | 104 | 805 | 640 | 177 | 0 | 58 | 2 | 1 | 402 | 0 | 8.24 | 0 | 9.74 | 17.98
Average | 16110.8065 | 16202.2258 | 447.3226 | 100.6452 | 2065.4474 | 1258.4194 | 1187.3871 | 2509.7097 | 4999.0494 | 2202.7742 | 903.2258 | 618.3952 | 12.0645 | 1.9677 | 9.9032 | 53.5161 | 55.1613 | 41.1935 | 97 | 136.3226 | 352.2581 | 78.0645 | 17.6129 | 95.3871 | 185 | 53.6452 | 16.871 | 37.9226 | 15.1419 | 0.0058065 | 3.6452 | 213.9677 | 206.4194 | 265.6129 | 290.9032 | 0 | 88.871 | 650.3548 | 447.3226 | 202.5013 | 0 | 58.1794 | 0.064516 | 0.074194 | 186.5032 | 7.441 | 2.1823 | 0.0074194 | 3.4087 | 5.5984
Total | 499435 | 502269 | 13867 | 3120 | 64028.87 | 39011 | 36809 | 77801 | 154970.53 | 68286 | 28000 | 19170.25 | 374 | 61 | 307 | 1659 | 1710 | 1277 | 3007 | 4226 | 10920 | 2420 | 546 | 2957 | 5735 | 1663 | 523 | 1175.6 | 469.4 | 0.18 | 113 | 6633 | 6399 | 8234 | 9018 | 0 | 2755 | 20161 | 13867 | 6277.54 | 0 | 1803.56 | 2 | 2.3 | 5781.6 | 230.67 | 67.65 | 0.23 | 105.67 | 173.55
[41 empty] | 0 | Today | 335
[40 empty] | HWG AVG | 168
20 cub extra
[40 empty] | INR | 773.6 | Extra

## 1
Daily Utility Consumption Report
Prepaired by- Nilesh | 2021-05-01 | occupancy | 84% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 30 | Last year same month avg
|  | humidity | 80%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 5727433 | 5743421 | 15988 | 15988 | 12000 | 15988
BEST supply |  |  | KVAH | 5761244 | 5777297 | 16053 | 16053 | 12000 | 16053
Transformer - 1 - 2500KVA |  |  | kwh | 990714 | 1006183 | 15469 | 15469 | -4053 | 15469
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 15469 | 15469 | 519 | 15469
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1670657 | 1670991 | 334 | 334 | 800 | 334
466
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 8 | 80 | 80 | 65 | 80
BMC |  |  | KL | 137812 | 137868 | 56 | 56 |  | 56
Total water | [5 empty] | 136 | 136 | -71 | 136
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 16053 | 9 | 144477 | 144477 |  | 144477
C.N.G |  |  | Cu.Mtr | 334 | 49 | 16366 | 16366 |  | 16366
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 56 | 134 | 7504 | 7504 |  | 7504
Water Tanker |  |  | KL | 80 | 80 | 6400 | 6400 |  | 6400
Total cost | [5 empty] | 174747 | 174747 |  | 174747
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 886459 | 888627 | 2168 | 2168 |  | 2168
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 344608 | 344999 | 391 | 391 |  | 391
Fire Emergency Power Panel - 1000A |  |  | kwh | 95225 | 96507 | 1282 | 1282 |  | 1282
Main Power Panel -1600A |  |  | kwh | 119596 | 120948 | 1352 | 1352 |  | 1352
Main Lighting and Small power Panel |  |  | kwh | 246653 | 248577 | 1924 | 1924 |  | 1924
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 0.23 | 0.23 | 0 | 0 |  | 0
Chiller No 1 |  |  | kwh | 181528 | 186183 | 4655 | 4655 |  | 4655
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 973958 | 976277 | 2319 | 2319 |  | 2319
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 0 |  | 0
Sub Total | [5 empty] | 14091 | 14091 |  | 14091
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732 | -0.13 | -0.13 |  | -0.13
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 474536 | 475485 | 949 | 949 |  | 949
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 416311 | 416982 | 671 | 671 |  | 671
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 11378 | 11452 | 74 | 74 |  | 74
Chiller No -3 - 1200A |  |  | kwh | 346926 | 346926 | 0 | 0 |  | 0
Chiller No-4 - 1200A |  |  | Kwh | 589288.47 | 589288 | -0.47 | -0.47 |  | -0.47
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 46668 | 46668 | 0 | 0 |  | 0
Sub Total | [5 empty] | 1693.4 | 1693.4 | 203.6 | 1693.4
|  |  | Total TR1 & TR2 |  |  | 15784.4 | 15784.4 | -315.4 | 15784.4
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0 |  | 0
5th floor spa |  |  | KWh | 2359 | 2363 | 4 | 4 |  | 4
5th Floor |  |  | KWh | 153299 | 153510 | 211 | 211 |  | 211
12th Floor |  |  | KWh | 154599 | 154807 | 208 | 208 |  | 208
20th Floor |  |  | KWh | 48571 | 48842 | 271 | 271 |  | 271
27th Floor |  |  | KWh | 243174 | 243396 | 222 | 222 |  | 222
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 78994 | 79076 | 82 | 82 |  | 82
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0 |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855461 | 855478 | 17 | 17 |  | 17
Main kitchen power panel no 2 |  |  | KWh | 885876 | 885878 | 2 | 2 |  | 2
Prato kitchen power panel |  |  | KWh | 2279 | 2309 | 30 | 30 |  | 30
San- Qi Indian Kitchen |  |  | KWh | 10970 | 11024 | 54 | 54 |  | 54
San- Qi Japanese Kitchen |  |  | KWh | 5709 | 5766 | 57 | 57 |  | 57
The club kitchen |  |  | KWh | 701562 | 701612 | 50 | 50 |  | 50
AER Kitchen |  |  | KWh | 670025 | 670149 | 124 | 124 |  | 124
COLD ROOM'S |  |  | KWh | 826784 | 826973 | 189 | 189 |  | 189
Ball Room 1 kitchen |  |  | KWh | 516738 | 517132 | 394 | 394 |  | 394
Ball Room 2 kitchen |  |  | KWh | 636478 | 636559 | 81 | 81 |  | 81
B1 Laundry |  |  | kwh | 107612 | 107624 | 12 | 12 |  | 12
STP Electrical |  |  | kwh | 14771 | 15026 | 255 | 255 |  | 255
Cooling Tower |  |  | kwh | 480133 | 480848 | 715 | 715 |  | 715
Total | [5 empty] | 1980 | 1980 |  | 1980
MOCK Up Room |  |  | Kwh | 459267 | 459318 | 51 | 51 |  | 51
27th Floor |  |  | Kwh | 80919 | 80929 | 10 | 10 |  | 10
Physic57 |  |  | Kwh | 151805 | 151833 | 28 | 28 |  | 28
Pinoor Legal- Power |  |  | Kwh | 64834 | 64841 | 7 | 7 |  | 7
Pinoor Legal- Lighting |  |  | Kwh | 3272 | 3272 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27907 | 27910 | 3 | 3
WATER
R.o.plant |  |  | KL | 244524 | 244576 | 52 | 52 |  | 52
STP Water Prod |  |  | KL | 183531 | 183626 | 95 | 95 |  | 95
Total water Produce | [5 empty] | 147
Domestic Zone-1 |  |  | KL | 412886 | 412958 | 72 | 72 |  | 72
Domestic Zone-2 |  |  | KL | 102343 | 102355 | 12 | 12 |  | 12
Domestic Zone-3 |  |  | KL | 97427 | 97444 | 17 | 17 |  | 17
Flush Zone -1 |  |  | KL | 149533 | 149538 | 5 | 5 |  | 5
Flush Zone -2 |  |  | KL | 7185 | 7190 | 5 | 5 |  | 5
Flush Zone -3 |  |  | KL | 5138 | 5144 | 6 | 6 |  | 6
Total water consum | [5 empty] | 117 | 117 |  | 117
Water Branches
Branches
Swimming pool |  |  | KL | 7431 | 7431 | 0 | 0 |  | 0
B2 Laundry |  |  | KL | 35828 | 35828 | 0 | 0 |  | 0
Boiler Feed Water |  |  | KL | 19617 | 19617 | 0 | 0 |  | 85
Total | [5 empty] | 0 | 0 |  | 0
Branches ( STP Water ) |  |  | KL |  |  |  | 0
cooling tower filling water |  |  | KL | 61174 | 61259 | 85 | 85 |  | 85
STP flush(new water meter) |  |  | KL | 32235 | 32235 | 0 | 0 |  | 0
Garden Water Pump |  |  | KL | 4368 | 4395 | 27 | 27 |  | 27
Total | [5 empty] | 112 | 112 |  | 112
Flushing Water | [6 empty] | 0 |  | 0
Flush Zone 2 pump meter |  |  | KL | 11259 | 11268 | 9 | 9 |  | 9
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8126 | 8131 | 5 | 5 |  | 5
Flush Tanker |  |  | KL |  |  | 0 | 0 |  | 0
Total | [5 empty] | 14 | 14 |  | 14
Total Domestic Water (R.O +BMC) |  |  | KL |  | 108 | 108 | 108 |  | 108
Total Domestic Consumption |  |  | KL |  | 112 | 112 | 112 |  | 112
Total STP Consumption |  |  | KL |  | 112 | 112 | 112 |  | 112
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 826088.46 | 826321 | 232.54 | 232.54 |  | 232.54
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 144687.44 | 144747 | 59.56 | 59.56 |  | 59.56
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8969.7 | 8970 | 0.3 | 0.3 |  | 0.3
Boiler Gas Consumption | [5 empty] | 41.6 | 41.6 |  | 41.6
Running Hrs
DG Set - 1 |  |  | hr |  | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr |  | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 39746.48 | 39770.33 | 23.85 | 23.85 |  | 23.85
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 |  | 0
Chiller - 3 |  |  | hr | 41385 | 41385 | 0 | 0 |  | 0
Chiller - 4 |  |  | hr | 32583 | 32583 | 0 | 0 | 23.85 | 0
Steam Boiler -1 |  |  | hr | 22739.59 | 22739.59 | 0 | 0 |  | 0
Steam Boiler -2 |  |  | hr | 25051.59 | 25051.59 | 0 | 0 |  | 0
Steam Boiler -3 |  |  | hr | 70315.81 | 70315.81 | 0 | 0 | 0 | 0
Hot Water Generator -1 |  |  | hr | 1616.86 | 1625.74 | 8.88 | 8.88 |  | 8.88
Hot Water Generator -2 |  |  | hr | 4637 | 4637 | 0 | 0 | 8.88 | 0
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4486.87 | 4486.87 |  | 4486.87
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 28.06% | 0.28064 |  | 0.28064
Total Chillers Units |  |  | kwh |  |  | 4654.53 | 4654.53 |  | 4654.53
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 29.11% | 0.29113 |  | 0.29113
Total Lighting Units |  |  | kwh |  |  | 2595 | 2595 |  | 2595
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 16.23% | 0.16231 |  | 0.16231
Total power Units |  |  | Kwh |  |  | 1352 | 1352 |  | 1352
% of power Units of Total Con.(LT) |  |  | % |  |  | 8.456% | 0.084563 |  | 0.084563
Total mansion power Units |  |  | Kwh |  |  | 1340 | 1340 |  | 1340
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 8.381% | 0.083813 |  | 0.083813
Total fire & em, power Units |  |  | Kwh |  |  | 1282 | 1282 |  | 1282
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 8.019% | 0.080185 |  | 0.080185
Lower Basement |  |  | KWh | 35932 | 36012 | 80
upper basement |  |  | KWh | 82358 | 82806 | 448
Level 1 |  |  | KWh | 38300 | 38569 | 269
Level 2 |  |  | KWh | 6219 | 6241 | 22
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2359 | 2363 | 4
5th Floor |  |  | KWh | 153299 | 153510 | 211
12th Floor |  |  | KWh | 154599 | 154807 | 208
20th Floor |  |  | KWh | 48571 | 48842 | 271
27th Floor |  |  | KWh | 243174 | 243396 | 222
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 78994 | 79076 | 82
1817

## 2
Daily Utility Consumption Report
Prepaired by- Nilesh | 2021-05-02 | occupancy | 60% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 30 | Last year same month avg
|  | humidity | 80%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 5743421 | 5759382 | 15961 | 31949 | 12000 | 15974.5
BEST supply |  |  | KVAH | 5777297 | 5793328 | 16031 | 32084 | 12000 | 16042
Transformer - 1 - 2500KVA |  |  | kwh | 1006183 | 1021632 | 15449 | 30918 | -4042 | 15459
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 37000 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 15449 | 30918 | 512 | 15459
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1670991 | 1671436 | 445 | 779 | 800 | 389.5
[8 empty] | 410.5 |  | 295
WATER CONSUMPTION
Tankers |  |  | KL | 8 | 6 | 60 | 140 | 65 | 70
BMC |  |  | KL | 137868 | 137919 | 51 | 107 |  | 53.5
Total water | [5 empty] | 111 | 247 | -58.5 | 123.5
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 1900 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 16031 | 9 | 144279 | 288756 |  | 144378
C.N.G |  |  | Cu.Mtr | 445 | 49 | 21805 | 38171 |  | 19085.5
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 51 | 134 | 6834 | 14338 |  | 7169
Water Tanker |  |  | KL | 60 | 80 | 4800 | 11200 |  | 5600
Total cost | [5 empty] | 177718 | 352465 |  | 176232.5
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 888627 | 890635 | 2008 | 4176 |  | 2088
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 344999 | 345384 | 385 | 776 |  | 388
Fire Emergency Power Panel - 1000A |  |  | kwh | 96507 | 97771 | 1264 | 2546 |  | 1273
Main Power Panel -1600A |  |  | kwh | 120948 | 122249 | 1301 | 2653 |  | 1326.5
Main Lighting and Small power Panel |  |  | kwh | 248577 | 250465 | 1888 | 3812 |  | 1906
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 0.23 | 0.23 | 0 | 0 |  | 0
Chiller No 1 |  |  | kwh | 186183 | 191184 | 5001 | 9656 |  | 4828
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 976277 | 978508 | 2231 | 4550 |  | 2275
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 0 |  | 0
Sub Total | [5 empty] | 14078 | 28169 |  | 14084.5
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732 | 260732.13 | 0.13 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 475485 | 476369 | 884 | 1833 |  | 916.5
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 416982 | 417535 | 553 | 1224 |  | 612
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 11452 | 11526 | 74 | 148 |  | 74
Chiller No -3 - 1200A |  |  | kwh | 346926 | 346926 | 0 | 0 |  | 0
Chiller No-4 - 1200A |  |  | Kwh | 589288 | 589288 | 0 | -0.47 |  | -0.235
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 46668 | 46781 | 113 | 113 |  | 56.5
Sub Total | [5 empty] | 1624.13 | 3317.53 | 258.87 | 1658.765
|  |  | Total TR1 & TR2 |  |  | 15702.13 | 31486.53 | -253.13 | 15743.265
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0 |  | 0
5th floor spa |  |  | KWh | 2363 | 2367 | 4 | 8 |  | 4
5th Floor |  |  | KWh | 153510 | 153718 | 208 | 419 |  | 209.5
12th Floor |  |  | KWh | 154807 | 155006 | 199 | 407 |  | 203.5
20th Floor |  |  | KWh | 48842 | 49114 | 272 | 543 |  | 271.5
27th Floor |  |  | KWh | 243396 | 243610 | 214 | 436 |  | 218
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79076 | 79169 | 93 | 175 |  | 87.5
Consumption of Extra AHU run |  |  | KWh
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855478 | 855493 | 15 | 32 |  | 16
Main kitchen power panel no 2 |  |  | KWh | 885878 | 885879 | 1 | 3 |  | 1.5
Prato kitchen power panel |  |  | KWh | 2309 | 2325 | 16 | 46 |  | 23
San- Qi Indian Kitchen |  |  | KWh | 11024 | 11076 | 52 | 106 |  | 53
San- Qi Japanese Kitchen |  |  | KWh | 5766 | 5822 | 56 | 113 |  | 56.5
The club kitchen |  |  | KWh | 701612 | 701659 | 47 | 97 |  | 48.5
AER Kitchen |  |  | KWh | 670149 | 670244 | 95 | 219 |  | 109.5
COLD ROOM'S |  |  | KWh | 826973 | 827150 | 177 | 366 |  | 183
Ball Room 1 kitchen |  |  | KWh | 517132 | 517512 | 380 | 774 |  | 387
Ball Room 2 kitchen |  |  | KWh | 636559 | 636625 | 66 | 147 |  | 73.5
B1 Laundry |  |  | kwh | 107624 | 107638 | 14 | 26 |  | 13
STP Electrical |  |  | kwh | 15026 | 15267 | 241 | 496 |  | 248
Cooling Tower |  |  | kwh | 480848 | 481560 | 712 | 1427 |  | 713.5
Total |  |  |  | 0 |  | 1872 | 3852 |  | 1926
MOCK Up Room |  |  | Kwh | 459318 | 459339 | 21 | 72 |  | 36
27th Floor |  |  | Kwh | 80929 | 80935 | 6 | 16 |  | 8
Physic57 |  |  | Kwh | 151833 | 151857 | 24 | 52 |  | 26
Pinoor Legal- Lighting |  |  | Kwh | 64841 | 64847 | 6 | 13 |  | 6.5
Pinoor Legal- Lighting |  |  | Kwh | 3272 | 3272 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27910 | 27911.65 | 1.65
WATER
R.o.plant |  |  | KL | 244576 | 244612 | 36 | 88 |  | 44
STP Water Prod |  |  | KL | 183626 | 183727 | 101 | 196 |  | 98
Total water Produce |  |  |  | 0 |  | 137 | 137 |  | 68.5
Domestic Zone-1 |  |  | KL | 412958 | 413000 | 42 | 114 |  | 57
Domestic Zone-2 |  |  | KL | 102355 | 102367 | 12 | 24 |  | 12
Domestic Zone-3 |  |  | KL | 97444 | 97462 | 18 | 35 |  | 17.5
Flush Zone -1 |  |  | KL | 149538 | 149543 | 5 | 10 |  | 5
Flush Zone -2 |  |  | KL | 7190 | 7195 | 5 | 10 |  | 5
Flush Zone -3 |  |  | KL | 5144 | 5150 | 6 | 12 |  | 6
Total water consum | [5 empty] | 88 | 205 |  | 102.5
Water Branches
Branches
Swimming pool |  |  | KL | 7431 | 7431 | 0 | 0 |  | 0
B2 Laundry |  |  | KL | 35828 | 35836 | 8 | 8 |  | 4
Boiler Feed Water |  |  | KL | 19617 | 19620 | 3 | 3 |  | 1.5
Total | [5 empty] | 11 | 11 |  | 5.5
Branches ( STP Water ) |  |  | KL |  |  |  | 0
cooling tower filling water |  |  | KL | 61259 | 61299 | 40 | 125 |  | 62.5
STP flush(new water meter) |  |  | KL | 32235 | 32235 | 0 | 0 |  | 0
Garden Water Pump |  |  | KL | 4395 | 4395 | 0 | 27 |  | 13.5
Total | [5 empty] | 40 | 152 |  | 76
Flushing Water | [6 empty] | 0 |  | 0
Flush Zone 2 pump meter |  |  | KL | 11268 | 11272 | 4 | 13 |  | 6.5
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8131 | 8135 | 4 | 9 |  | 4.5
Flush Tanker |  |  | KL |  |  | 0 | 0 |  | 0
Total | [5 empty] | 8 | 22 |  | 11
Total Domestic Water (R.O +BMC) |  |  | KL |  | 87 | 87 | 195 |  | 97.5
Total Domestic Consumption |  |  | KL |  | 83 | 83 | 195 |  | 97.5
Total STP Consumption |  |  | KL |  | 40 | 40 | 152 |  | 76
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 826321 | 826524 | 203 | 435.54 |  | 217.77
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 144747 | 144820 | 73 | 132.56 |  | 66.28
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970 | 8970 | 0 | 0.3 |  | 0.15
Boiler Gas Consumption | [5 empty] | 169 | 210.6 |  | 105.3
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 39770.33 | 39794.31 | 23.98 | 47.83 |  | 23.915
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 23.98 | 0
Chiller - 3 |  |  | hr | 41385 | 41385 | 0 | 0 |  | 0
Chiller - 4 |  |  | hr | 32583 | 32583 | 0 | 0 |  | 0
Steam Boiler -1 |  |  | hr | 22739.59 | 22742.3 | 2.71 | 2.71 |  | 1.355
Steam Boiler -2 |  |  | hr | 25051.59 | 25051.59 | 0 | 0 |  | 0
Steam Boiler -3 |  |  | hr | 70315.81 | 70315.81 | 0 | 0 | 2.71 | 0
Hot Water Generator -1 |  |  | hr | 1625.74 | 1633.55 | 7.81 | 16.69 |  | 8.345
Hot Water Generator -2 |  |  | hr | 4637 | 4637 | 0 | 0 | 7.81 | 0
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4239.13 | 8726 |  | 4363
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 26.56% | 0.54623 |  | 0.27312
Total Chillers Units |  |  | kwh |  |  | 5001 | 9655.53 |  | 4827.765
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 31.33% | 0.60445 |  | 0.30223
Total Lighting Units |  |  | kwh |  |  | 2441 | 5036 |  | 2518
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 15.29% | 0.31524 |  | 0.15762
Total power Units |  |  | Kwh |  |  | 1301 | 2653 |  | 1326.5
% of power Units of Total Con.(LT) |  |  | % |  |  | 8.151% | 0.16607 |  | 0.083037
Total mansion power Units |  |  | Kwh |  |  | 1269 | 2609 |  | 1304.5
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 7.951% | 0.16332 |  | 0.08166
Total fire & em, power Units |  |  | Kwh |  |  | 1264 | 2546 |  | 1273
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.919% | 0.15938 |  | 0.079689
Main Lighting & Small power pannel Sub meter
Lower Basement |  |  | KWh | 36012 | 36093 | 81
upper basement |  |  | KWh | 82806 | 83235 | 429
Level 1 |  |  | KWh | 38569 | 38792 | 223
Level 2 |  |  | KWh | 6241 | 6245 | 4
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2363 | 2367 | 4
5th Floor |  |  | KWh | 153510 | 153718 | 208
12th Floor |  |  | KWh | 154807 | 155006 | 199
20th Floor |  |  | KWh | 48842 | 49114 | 272
27th Floor |  |  | KWh | 243396 | 243610 | 214
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79076 | 79169 | 93

## 3
Daily Utility Consumption Report
Prepaired by--- Nilesh | 2021-05-03 | occupancy | 57% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 29 | Last year same month avg
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 5759382 | 5775411 | 16029 | 47978 | 12000 | 15992.6667
BEST supply |  |  | KVAH | 5793328 | 5809417 | 16089 | 48173 | 12000 | 16057.6667
Transformer - 1 - 2500KVA |  |  | kwh | 1021632 | 1037141 | 15509 | 46427 | -4057.6667 | 15475.6667
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 15509 | 46427 | 520 | 15475.6667
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1671436 | 1671874 | 438 | 1217 | 800 | 405.6667
394.3333
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 6 | 60 | 200 | 65 | 66.6667
BMC |  |  | KL | 137919 | 137975 | 56 | 163 |  | 54.3333
Total water | [5 empty] | 116 | 363 | -56 | 121
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 16089 | 9 | 144801 | 433557 |  | 144519
C.N.G |  |  | Cu.Mtr | 438 | 49 | 21462 | 59633 |  | 19877.6667
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 56 | 134 | 7504 | 21842 |  | 7280.6667
Water Tanker |  |  | KL | 60 | 80 | 4800 | 16000 |  | 5333.3333
Total cost | [5 empty] | 178567 | 531032 |  | 177010.6667
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 890635 | 892809 | 2174 | 6350 |  | 2116.6667
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 345384 | 345750 | 366 | 1142 |  | 380.6667
Fire Emergency Power Panel - 1000A |  |  | kwh | 97771 | 98995 | 1224 | 3770 |  | 1256.6667
Main Power Panel -1600A |  |  | kwh | 122249 | 123591 | 1342 | 3995 |  | 1331.6667
Main Lighting and Small power Panel |  |  | kwh | 250465 | 252272 | 1807 | 5619 |  | 1873
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 0.23 | 0.23 | 0 | 0 |  | 0
Chiller No 1 |  |  | kwh | 191184 | 196005 | 4821 | 14477 |  | 4825.6667
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 978508 | 980728 | 2220 | 6770 |  | 2256.6667
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 0 |  | 0
Sub Total | [5 empty] | 13954 | 42123 |  | 14041
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732 | -0.13 | -0.13 |  | -0.043333
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 476369 | 477425 | 1056 | 2889 |  | 963
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 417535 | 418065 | 530 | 1754 |  | 584.6667
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 11526 | 11600 | 74 | 222 |  | 74
Chiller No -3 - 1200A |  |  | kwh | 346926 | 346926 | 0 | 0 |  | 0
Chiller No-4 - 1200A |  |  | Kwh | 589288 | 589288 | 0 | -0.47 |  | -0.15667
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 46781 | 46872 | 91 | 204 |  | 68
Sub Total | [5 empty] | 1750.87 | 5068.4 | 324.13 | 1689.4667
|  |  | Total TR1 & TR2 |  |  | 15704.87 | 47191.4 | -195.87 | 15730.4667
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0 |  | 0
5th floor spa |  |  | KWh | 2367 | 2370 | 3 | 11 |  | 3.6667
5th Floor |  |  | KWh | 153718 | 153931 | 213 | 632 |  | 210.6667
12th Floor |  |  | KWh | 155006 | 155204 | 198 | 605 |  | 201.6667
20th Floor |  |  | KWh | 49114 | 49379 | 265 | 808 |  | 269.3333
27th Floor |  |  | KWh | 243610 | 243795 | 185 | 621 |  | 207
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79169 | 79254 | 85 | 260 |  | 86.6667
Consumption of Extra AHU run |  |  | KWh
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855493 | 855508 | 15 | 47 |  | 15.6667
Main kitchen power panel no 2 |  |  | KWh | 885879 | 885880 | 1 | 4 |  | 1.3333
Prato kitchen power panel |  |  | KWh | 2325 | 2340 | 15 | 61 |  | 20.3333
San- Qi Indian Kitchen |  |  | KWh | 11076 | 11130 | 54 | 160 |  | 53.3333
San- Qi Japanese Kitchen |  |  | KWh | 5822 | 5876 | 54 | 167 |  | 55.6667
The club kitchen |  |  | KWh | 701659 | 701709 | 50 | 147 |  | 49
AER Kitchen |  |  | KWh | 670244 | 670345 | 101 | 320 |  | 106.6667
COLD ROOM'S |  |  | KWh | 827150 | 827324 | 174 | 540 |  | 180
Ball Room 1 kitchen |  |  | KWh | 517512 | 517871 | 359 | 1133 |  | 377.6667
Ball Room 2 kitchen |  |  | KWh | 636625 | 636693 | 68 | 215 |  | 71.6667
B1 Laundry |  |  | kwh | 107638 | 107663 | 25 | 51 |  | 17
STP Electrical |  |  | kwh | 15267 | 15516 | 249 | 745 |  | 248.3333
Cooling Tower |  |  | kwh | 481560 | 482378 | 818 | 2245 |  | 748.3333
Total |  |  |  | 0 |  | 1983 | 5835 |  | 1945
MOCK Up Room |  |  | Kwh | 459339 | 459523 | 184 | 256 |  | 85.3333
27th Floor |  |  | Kwh | 80935 | 80949 | 14 | 30 |  | 10
Physic57 |  |  | Kwh | 151857 | 152003 | 146 | 198 |  | 66
Pinoor Legal- Lighting |  |  | Kwh | 64847 | 64853 | 6 | 19 |  | 6.3333 | #VALUE!
Pinoor Legal- Lighting |  |  | Kwh | 3272 | 3272 | 0 | 0 |  | 0 | #VALUE!
20th Floor Project office |  |  |  | 27911.65 | 27914.1 | 2.45
WATER
R.o.plant |  |  | KL | 244612 | 244664 | 52 | 140 |  | 46.6667
STP Water Prod |  |  | KL | 183727 | 183838 | 111 | 307 |  | 102.3333
Total water Produce |  |  |  | 0 |  | 163 | 300 |  | 100
Domestic Zone-1 |  |  | KL | 413000 | 413061 | 61 | 175 |  | 58.3333
Domestic Zone-2 |  |  | KL | 102367 | 102384 | 17 | 41 |  | 13.6667
Domestic Zone-3 |  |  | KL | 97462 | 97477 | 15 | 50 |  | 16.6667
Flush Zone -1 |  |  | KL | 149543 | 149547 | 4 | 14 |  | 4.6667
Flush Zone -2 |  |  | KL | 7195 | 7199 | 4 | 14 |  | 4.6667
Flush Zone -3 |  |  | KL | 5150 | 5155 | 5 | 17 |  | 5.6667
Total water consum | [5 empty] | 106 | 311 |  | 103.6667
Water Branches
Branches
Swimming pool |  |  | KL | 7431 | 7431 | 0 | 0 |  | 0
B2 Laundry |  |  | KL | 35836 | 35836 | 0 | 8 |  | 2.6667
Boiler Feed Water |  |  | KL | 19620 | 19623 | 3 | 6 |  | 2
Total |  |  |  |  | . | 3 | 14 |  | 4.6667
Branches ( STP Water ) |  |  | KL |  |  |  | 0
cooling tower filling water |  |  | KL | 61299 | 61340 | 41 | 166 |  | 55.3333
STP flush(new water meter) |  |  | KL | 32235 | 32235 | 0 | 0 |  | 0
Garden Water Pump |  |  | KL | 4395 | 4417 | 22 | 49 |  | 16.3333
Total | [5 empty] | 63 | 215 |  | 71.6667
Flushing Water | [6 empty] | 0 |  | 0
Flush Zone 2 pump meter |  |  | KL | 11272 | 11278 | 6 | 19 |  | 6.3333
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8135 | 8139 | 4 | 13 |  | 4.3333
Flush Tanker |  |  | KL |  |  | 0 | 0 |  | 0
Total | [5 empty] | 10 | 32 |  | 10.6667
Total Domestic Water (R.O +BMC) |  |  | KL |  | 108 | 108 | 303 |  | 101
Total Domestic Consumption |  |  | KL |  | 102 | 102 | 297 |  | 99
Total STP Consumption |  |  | KL |  | 63 | 63 | 215 |  | 71.6667
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 826524 | 826721 | 197 | 632.54 |  | 210.8467
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583 | -0.4 | -0.4 |  | -0.13333
BallRoom Gas |  |  | m3 | 144820 | 144878 | 58 | 190.56 |  | 63.52
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970 | 8970 | 0 | 0.3 |  | 0.1
Boiler Gas Consumption |  |  |  | 0 |  | 183.4 | 394 |  | 131.3333
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 39794.31 | 39818.31 | 24 | 71.83 |  | 23.9433
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 |  | 0
Chiller - 3 |  |  | hr | 41385 | 41385 | 0 | 0 |  | 0
Chiller - 4 |  |  | hr | 32583 | 32583 | 0 | 0 | 24 | 0
Steam Boiler -1 |  |  | hr | 22742.3 | 22742.3 | 0 | 2.71 |  | 0.90333
Steam Boiler -2 |  |  | hr | 25051.59 | 25051.99 | 0.4 | 0.4 |  | 0.13333
Steam Boiler -3 |  |  | hr | 70315.81 | 70324.82 | 9.01 | 9.01 | 9.41 | 3.0033
Hot Water Generator -1 |  |  | hr | 1633.55 | 1640.95 | 7.4 | 24.09 |  | 8.03
Hot Water Generator -2 |  |  | hr | 4637 | 4637 | 0 | 0 | 0 | 0
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4393.87 | 13119.87 |  | 4373.29
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 27.41% | 0.82035 |  | 0.27345
Total Chillers Units |  |  | kwh |  |  | 4821 | 14476.53 |  | 4825.51
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 30.08% | 0.90522 |  | 0.30174
Total Lighting Units |  |  | kwh |  |  | 2337 | 7373 |  | 2457.6667
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 14.58% | 0.46104 |  | 0.15368
Total power Units |  |  | Kwh |  |  | 1342 | 3995 |  | 1331.6667
% of power Units of Total Con.(LT) |  |  | % |  |  | 8.372% | 0.2498 |  | 0.083266
Total mansion power Units |  |  | Kwh |  |  | 1422 | 4031 |  | 1343.6667
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 8.871% | 0.25203 |  | 0.084011
Total fire & em, power Units |  |  | Kwh |  |  | 1224 | 3770 |  | 1256.6667
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.636% | 0.23574 |  | 0.07858
Main Lighting & Small power pannel Sub meter
Lower Basement |  |  | KWh | 36093 | 36175 | 82
upper basement |  |  | KWh | 83235 | 83633 | 398
Level 1 |  |  | KWh | 38792 | 38999 | 207
Level 2 |  |  | KWh | 6245 | 6255 | 10
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2367 | 2370 | 3
5th Floor |  |  | KWh | 153718 | 153931.9 | 213.9
12th Floor |  |  | KWh | 155006 | 155204 | 198
20th Floor |  |  | KWh | 49114 | 49379 | 265
27th Floor |  |  | KWh | 243610 | 243795 | 185
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79169 | 79254 | 85

## 4
Daily Utility Consumption Report
Prepaired by-- Devendra | 2021-05-04 | occupancy | 10% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 34 | Last year same month avg
|  | humidity | 84%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 5775411 | 5791574 | 16163 | 64141 | 12000 | 16035.25
BEST supply |  |  | KVAH | 5809417 | 5825643 | 16226 | 64399 | 12000 | 16099.75 |  | 0.99612
Transformer - 1 - 2500KVA |  |  | kwh | 1037141 | 1052790 | 15649 | 62076 | -4099.75 | 15519
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 15649 | 62076 | 514 | 15519
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1671874 | 1672458 | 584 | 1801 | 800 | 450.25
349.75
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 6 | 60 | 260 | 65 | 65
BMC |  |  | KL | 137975 | 138022 | 47 | 210 |  | 52.5
Total water |  |  |  | 0 |  | 107 | 470 | -52.5 | 117.5
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0 | `
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 16226 | 9 | 146034 | 579591 |  | 144897.75
C.N.G |  |  | Cu.Mtr | 584 | 49 | 28616 | 88249 |  | 22062.25
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 47 | 134 | 6298 | 28140 |  | 7035
Water Tanker |  |  | KL | 60 | 80 | 4800 | 20800 |  | 5200
Total cost | [5 empty] | 185748 | 716780 |  | 179195
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 892809 | 894970 | 2161 | 8511 |  | 2127.75
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 345750 | 346095 | 345 | 1487 |  | 371.75
Fire Emergency Power Panel - 1000A |  |  | kwh | 98995 | 100208 | 1213 | 4983 |  | 1245.75
Main Power Panel -1600A |  |  | kwh | 123591 | 124846 | 1255 | 5250 |  | 1312.5
Main Lighting and Small power Panel |  |  | kwh | 252272 | 254017 | 1745 | 7364 |  | 1841
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 0.23 | 0 | -0.23 | -0.23 |  | -0.0575
Chiller No 1 |  |  | kwh | 196005 | 201104 | 5099 | 19576 |  | 4894
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 980728 | 982927 | 2199 | 8969 |  | 2242.25
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 0 |  | 0
Sub Total | [5 empty] | 14016.77 | 56139.77 |  | 14034.9425
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732 | 260732 | 0 | -0.13 |  | -0.0325
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 477425 | 478454 | 1029 | 3918 |  | 979.5
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 418065 | 418571 | 506 | 2260 |  | 565
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 11600 | 11672 | 72 | 294 |  | 73.5
Chiller No -3 - 1200A |  |  | kwh | 346926 | 346926 | 0 | 0 |  | 0
Chiller No-4 - 1200A |  |  | Kwh | 589288 | 589336 | 48 | 47.53 |  | 11.8825
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 46872 | 47090 | 218 | 422 |  | 105.5
Sub Total | [5 empty] | 1873 | 6941.4 | 273.23 | 1735.35
|  |  | Total TR1 & TR2 |  |  | 15889.77 | 63081.17 | -240.77 | 15770.2925
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 0 | 0 | 0 | 0.002 |  | 0.0005
5th floor spa |  |  | KWh | 2370 | 2374 | 4 | 15 |  | 3.75
5th Floor |  |  | KWh | 153931 | 154137 | 206 | 838 |  | 209.5
12th Floor |  |  | KWh | 155204 | 155406 | 202 | 807 |  | 201.75
20th Floor |  |  | KWh | 49379 | 49645 | 266 | 1074 |  | 268.5
27th Floor |  |  | KWh | 243795 | 243946 | 151 | 772 |  | 193
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79254 | 79332 | 78 | 338 |  | 84.5
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0 |  | 0
Main kitchen power panel no 1 |  |  | KWh | 855508 | 855525 | 17 | 64 |  | 16
Main kitchen power panel no 2 |  |  | KWh | 885880 | 885881 | 1 | 5 |  | 1.25
Prato kitchen power panel |  |  | KWh | 2340 | 2351 | 11 | 72 |  | 18
San- Qi Indian Kitchen |  |  | KWh | 11130 | 11181 | 51 | 211 |  | 52.75
San- Qi Japanese Kitchen |  |  | KWh | 5876 | 5930 | 54 | 221 |  | 55.25
The club kitchen |  |  | KWh | 701709 | 701760 | 51 | 198 |  | 49.5
AER Kitchen |  |  | KWh | 670345 | 670400 | 55 | 375 |  | 93.75
COLD ROOM'S |  |  | KWh | 827324 | 827512 | 188 | 728 |  | 182
Ball Room 1 kitchen |  |  | KWh | 517871 | 518233 | 362 | 1495 |  | 373.75
Ball Room 2 kitchen |  |  | KWh | 636693 | 636768 | 75 | 290 |  | 72.5
B1 Laundry |  |  | kwh | 107663 | 107675 | 12 | 63 |  | 15.75
STP Electrical |  |  | kwh | 15516 | 15695 | 179 | 924 |  | 231
Cooling Tower |  |  | kwh | 482378 | 483194 | 816 | 3061 |  | 765.25
Total | [5 empty] | 1872 | 7707 |  | 1926.75
MOCK Up Room |  |  | Kwh | 459523 | 459766 | 243 | 499 |  | 124.75
27th Floor |  |  | Kwh | 80949 | 80961 | 12 | 42 |  | 10.5
Physic57 |  |  | Kwh | 152003 | 152033 | 30 | 228 |  | 57
Pinoor Legal- Lighting |  |  | Kwh | 64853 | 64860 | 7 | 26 |  | 6.5
Pinoor Legal- Lighting |  |  | Kwh | 3272 | 3272 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27914.1 | 27916.53 | 2.43 | 2.43 |  | 0.6075
WATER
R.o.plant |  |  | KL | 244664 | 244703 | 39 | 179 |  | 44.75
STP Water Prod |  |  | KL | 183838 | 183909 | 71 | 378 |  | 94.5
Total water Produce | [5 empty] | 110 | 410 |  | 102.5
Domestic Zone-1 |  |  | KL | 413061 | 413123 | 62 | 237 |  | 59.25
Domestic Zone-2 |  |  | KL | 102384 | 102393 | 9 | 50 |  | 12.5
Domestic Zone-3 |  |  | KL | 97477 | 97495 | 18 | 68 |  | 17
Flush Zone -1 |  |  | KL | 149547 | 149553 | 6 | 20 |  | 5
Flush Zone -2 |  |  | KL | 7199 | 7202 | 3 | 17 |  | 4.25
Flush Zone -3 |  |  | KL | 5155 | 5169 | 14 | 31 |  | 7.75
Total water consum | [5 empty] | 112 | 423 |  | 105.75
Water Branches
Branches
Swimming pool |  |  | KL | 7431 | 7431 | 0 | 0 |  | 0
B2 Laundry |  |  | KL | 35836 | 35847 | 11 | 19 |  | 4.75
Boiler Feed Water |  |  | KL | 19623 | 19632 | 9 | 15 |  | 3.75
Total |  |  |  | . |  | 20 | 34 |  | 8.5
Branches ( STP Water ) |  |  | KL | 0 |  |  | 0
cooling tower filling water |  |  | KL | 61340 | 61400 | 60 | 226 |  | 56.5
STP flush(new water meter) |  |  | KL | 32235 | 32245 | 10 | 10 |  | 2.5
Garden Water Pump |  |  | KL | 4417 | 4417 | 0 | 49 |  | 12.25
Total |  |  |  | 0 |  | 70 | 285 |  | 71.25
Flushing Water |  |  |  | 0 |  |  | 0 |  | 0
Flush Zone 2 pump meter |  |  | KL | 11278 | 11283 | 5 | 24 |  | 6
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8139 | 8143 | 4 | 17 |  | 4.25
Flush Tanker |  |  | KL |  |  | 0 | 0 |  | 0
Total | [5 empty] | 9 | 41 |  | 10.25
Total Domestic Water (R.O +BMC) |  |  | KL |  | 86 | 86 | 389 |  | 97.25
Total Domestic Consumption |  |  | KL |  | 106 | 106 | 403 |  | 100.75
Total STP Consumption |  |  | KL |  | 70 | 70 | 285 |  | 71.25
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 826721 | 826910 | 189 | 821.54 |  | 205.385
Prato Kitchen Gas meter Reading |  |  | m3 | 73583 | 73583 | 0 | -0.4 |  | -0.1
BallRoom Gas |  |  | m3 | 144878 | 144923 | 45 | 235.56 |  | 58.89
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970 | 8970 | 0 | 0.3 |  | 0.075
Boiler Gas Consumption | [5 empty] | 350 | 744 |  | 186
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 39818.31 | 39842 | 23.69 | 95.52 |  | 23.88
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 23.69 | 0
Chiller - 3 |  |  | hr | 41385 | 41385 | 0 | 0 |  | 0
Chiller - 4 |  |  | hr | 32583 | 32583 | 0 | 0 |  | 0
Steam Boiler -1 |  |  | hr | 22742.3 | 22749.51 | 7.21 | 9.92 | 6.81 | 2.48
Steam Boiler -2 |  |  | hr | 25051.99 | 25051.59 | -0.4 | 0 |  | 0
Steam Boiler -3 |  |  | hr | 70324.82 | 70324.82 | 0 | 9.01 |  | 2.2525
Hot Water Generator -1 |  |  | hr | 1640.95 | 1648.08 | 7.13 | 31.22 | 7.13 | 7.805
Hot Water Generator -2 |  |  | hr | 4637 | 4637 | 0 | 0 |  | 0
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4360 | 17479.87 |  | 4369.9675
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 26.98% | 1.0901 |  | 0.27253
Total Chillers Units |  |  | kwh |  |  | 5147 | 19623.53 |  | 4905.8825
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 31.84% | 1.2237 |  | 0.30592
Total Lighting Units |  |  | kwh |  |  | 2251 | 9624 |  | 2406
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 13.93% | 0.60031 |  | 0.15008
Total power Units |  |  | Kwh |  |  | 1255 | 5250 |  | 1312.5
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.765% | 0.32744 |  | 0.081861
Total mansion power Units |  |  | Kwh |  |  | 1374 | 5405 |  | 1351.25
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 8.501% | 0.33704 |  | 0.084261
Total fire & em, power Units |  |  | Kwh |  |  | 1213 | 4983 |  | 1245.75
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.505% | 0.31079 |  | 0.077697
Main Lighting & Small power pannel Sub meter
Lower Basement |  |  | KWh | 36175 | 36257 | 82
upper basement |  |  | KWh | 83633 | 84066 | 433
Level 1 |  |  | KWh | 38999 | 39208 | 209
Level 2 |  |  | KWh | 6255 | 6261 | 6
2nd floor plant room |  |  | KWh | 0 | 0 | 0
5th floor spa |  |  | KWh | 2370 | 2374 | 4
5th Floor |  |  | KWh | 153931.9 | 154137 | 205.1
12th Floor |  |  | KWh | 155204 | 155406 | 202
20th Floor |  |  | KWh | 49379 | 49645 | 266
27th Floor |  |  | KWh | 243795 | 243946 | 151
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79254 | 79332 | 78

## 5
Daily Utility Consumption Report
Prepaired by --- Devendra | 2021-05-05 | occupancy | 11% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 34 | Last year same month avg
|  | humidity | 84%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | .. | 5791574 | 5807328 | 15754 | 79895 | 12000 | 15979
BEST supply |  |  | KVAH | 5825643 | 5841454 | 15811 | 80210 | 12000 | 16042
Transformer - 1 - 2500KVA |  |  | kwh | 1052790 | 1068028 | 15238 | 77314 | -4042 | 15462.8
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0 | 108
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0 | 28
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0 | 342
SubTotal | [5 empty] | 15238 | 77314 | 516 | 15462.8 | 349
GAS CONSUMPTION | [9 empty] | 432
Gas consumption |  |  | m3 | 1672458 | 1672745 | 287 | 2088 | 800 | 417.6
382.4
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 6 | 60 | 320 | 65 | 64
BMC |  |  | KL | 138022 | 138075 | 53 | 263 |  | 52.6
Total water | [5 empty] | 113 | 583 | -51.6 | 116.6
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 15811 | 9 | 142299 | 721890 |  | 144378
C.N.G |  |  | Cu.Mtr | 287 | 49 | 14063 | 102312 |  | 20462.4
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 53 | 134 | 7102 | 35242 |  | 7048.4
Water Tanker |  |  | KL | 60 | 80 | 4800 | 25600 |  | 5120
Total cost | [5 empty] | 168264 | 885044 |  | 177008.8
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 894970 | 897088 | 2118 | 10629 |  | 2125.8
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 346095 | 346435 | 340 | 1827 |  | 365.4
Fire Emergency Power Panel - 1000A |  |  | kwh | 100208 | 101398 | 1190 | 6173 |  | 1234.6
Main Power Panel -1600A |  |  | kwh | 124846 | 126054 | 1208 | 6458 |  | 1291.6
Main Lighting and Small power Panel |  |  | kwh | 254017 | 255727 | 1710 | 9074 |  | 1814.8
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 0 | 0 | 0 | -0.23 |  | -0.046
Chiller No 1 |  |  | kwh | 201104 | 206065 | 4961 | 24537 |  | 4907.4
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 982927 | 985171 | 2244 | 11213 |  | 2242.6
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 0 |  | 0
Sub Total | [5 empty] | 13771 | 69910.77 |  | 13982.154
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732 | 260732 | 0 | -0.13 |  | -0.026
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 478454 | 479444 | 990 | 4908 |  | 981.6
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 418571 | 419100 | 529 | 2789 |  | 557.8
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 11672 | 11743 | 71 | 365 |  | 73
Chiller No -3 - 1200A |  |  | kwh | 346926 | 346926 | 0 | 0 |  | 0
Chiller No-4 - 1200A |  |  | Kwh | 589336 | 589345 | 9 | 56.53 |  | 11.306
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 47090 | 47133 | 43 | 465 |  | 93
Sub Total | [5 empty] | 1642 | 8583.4 | 341 | 1716.68
|  |  | Total TR1 & TR2 |  |  | 15413 | 78494.17 | -175 | 15698.834
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 0 | 0 | 0 | 0.002 |  | 0.0004
5th floor spa |  |  | KWh | 2374 | 2378 | 4 | 19 |  | 3.8
5th Floor |  |  | KWh | 154137 | 154342 | 205 | 1043 |  | 208.6
12th Floor |  |  | KWh | 155406 | 155606 | 200 | 1007 |  | 201.4
20th Floor |  |  | KWh | 49645 | 49895 | 250 | 1324 |  | 264.8
27th Floor |  |  | KWh | 243946 | 244093 | 147 | 919 |  | 183.8
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79332 | 79402 | 70 | 408 |  | 81.6
Consumption of Extra AHU run |  |  | KWh
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855525 | 855540 | 15 | 79 |  | 15.8
Main kitchen power panel no 2 |  |  | KWh | 885881 | 885882 | 1 | 6 |  | 1.2
Prato kitchen power panel |  |  | KWh | 2351 | 2373 | 22 | 94 |  | 18.8
San- Qi Indian Kitchen |  |  | KWh | 11181 | 11231 | 50 | 261 |  | 52.2
San- Qi Japanese Kitchen |  |  | KWh | 5930 | 5979 | 49 | 270 |  | 54
The club kitchen |  |  | KWh | 701760 | 701807 | 47 | 245 |  | 49
AER Kitchen |  |  | KWh | 670400 | 670446 | 46 | 421 |  | 84.2
COLD ROOM'S |  |  | KWh | 827512 | 827689 | 177 | 905 |  | 181
Ball Room 1 kitchen |  |  | KWh | 518233 | 518572 | 339 | 1834 |  | 366.8
Ball Room 2 kitchen |  |  | KWh | 636768 | 636838 | 70 | 360 |  | 72
B1 Laundry |  |  | kwh | 107675 | 107685 | 10 | 73 |  | 14.6
STP Electrical |  |  | kwh | 15695 | 15884 | 189 | 1113 |  | 222.6
Cooling Tower |  |  | kwh | 483194 | 483976 | 782 | 3843 |  | 768.6
Total |  |  |  | 0 |  | 1797 | 9504 |  | 1900.8
MOCK Up Room |  |  | Kwh | 459766 | 459964 | 198 | 697 |  | 139.4 | 25
27th Floor |  |  | Kwh | 80961 | 80979 | 18 | 60 |  | 12 | 108
Physic57 |  |  | Kwh | 152033 | 152056 | 23 | 251 |  | 50.2 | 28
Pinoor Legal- Power |  |  | Kwh | 64860 | 64866 | 6 | 32 |  | 6.4 | 342
Pinoor Legal- Lighting |  |  | Kwh | 3272 | 3272 | 0 | 0 |  | 0 | 349
20th Floor Project office |  |  |  | 27916.53 | 27918.61 | 2.08
WATER
R.o.plant |  |  | KL | 244703 | 244729 | 26 | 205 |  | 41
STP Water Prod |  |  | KL | 183909 | 183978 | 69 | 447 |  | 89.4
Total water Produce | [5 empty] | 95 | 505 |  | 101
Domestic Zone-1 |  |  | KL | 413123 | 413154 | 31 | 268 |  | 53.6
Domestic Zone-2 |  |  | KL | 102393 | 102399 | 6 | 56 |  | 11.2
Domestic Zone-3 |  |  | KL | 97495 | 97506 | 11 | 79 |  | 15.8
Flush Zone -1 |  |  | KL | 149553 | 149560 | 7 | 27 |  | 5.4
Flush Zone -2 |  |  | KL | 7202 | 7205 | 3 | 20 |  | 4
Flush Zone -3 |  |  | KL | 5169 | 5190 | 21 | 52 |  | 10.4
Total water consum | [5 empty] | 79 | 502 |  | 100.4
Water Branches
Branches
Swimming pool |  |  | KL | 7431 | 7435 | 4 | 4 |  | 0.8
B2 Laundry |  |  | KL | 35847 | 35847 | 0 | 19 |  | 3.8
Boiler Feed Water |  |  | KL | 19632 | 19635 | 3 | 18 |  | 3.6
Total |  |  |  | . |  | 7 | 41 |  | 8.2
Branches ( STP Water ) |  |  | KL | 0 |  |  | 0
cooling tower filling water |  |  | KL | 61400 | 61439 | 39 | 265 |  | 53
STP flush(new water meter) |  |  | KL | 32245 | 32267 | 22 | 32 |  | 6.4
Garden Water Pump |  |  | KL | 4417 | 4441 | 24 | 73 |  | 14.6
Total | [5 empty] | 85 | 370 |  | 74
Flushing Water | [6 empty] | 0 |  | 0
Flush Zone 2 pump meter |  |  | KL | 11283 | 11286 | 3 | 27 |  | 5.4
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8143 | 8163 | 20 | 37 |  | 7.4
Flush Tanker |  |  | KL |  |  | 0 | 0 |  | 0
Total | [5 empty] | 23 | 64 |  | 12.8
Total Domestic Water (R.O +BMC) |  |  | KL | 382804 | 79 | 79 | 468 |  | 93.6
Total Domestic Consumption |  |  | KL | 625454 | 72 | 72 | 475 |  | 95
Total STP Consumption |  |  | KL | 0 | 85 | 85 | 370 |  | 74
0
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 826910 | 827112 | 202 | 1023.54 |  | 204.708
Prato Kitchen Gas meter Reading |  |  | m3 | 73583 | 73583 | 0 | -0.4 |  | -0.08
BallRoom Gas |  |  | m3 | 144923 | 144974 | 51 | 286.56 |  | 57.312
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970 | 8970 | 0 | 0.3 |  | 0.06
Boiler Gas Consumption | [5 empty] | 34 | 778 |  | 155.6
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 39842 | 39866 | 24 | 119.52 |  | 23.904
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 24 | 0
Chiller - 3 |  |  | hr | 41385 | 41385 | 0 | 0 |  | 0
Chiller - 4 |  |  | hr | 32583 | 32583 | 0 | 0 |  | 0
Steam Boiler -1 |  |  | hr | 22749.51 | 22749.51 | 0 | 9.92 | 0 | 1.984
Steam Boiler -2 |  |  | hr | 25051.59 | 25051.59 | 0 | 0 |  | 0
Steam Boiler -3 |  |  | hr | 70324.82 | 70324.82 | 0 | 9.01 |  | 1.802
Hot Water Generator -1 |  |  | hr | 1648.08 | 1655.82 | 7.74 | 38.96 | 7.74 | 7.792
Hot Water Generator -2 |  |  | hr | 4637 | 4637 | 0 | 0 |  | 0
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4362 | 21841.87 | . | 4368.374
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 27.69% | 1.367 |  | 0.2734
Total Chillers Units |  |  | kwh |  |  | 4970 | 24593.53 |  | 4918.706
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 31.55% | 1.5391 |  | 0.30783
Total Lighting Units |  |  | kwh |  |  | 2239 | 11863 |  | 2372.6
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 14.21% | 0.74243 |  | 0.14849
Total power Units |  |  | Kwh |  |  | 1208 | 6458 |  | 1291.6
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.668% | 0.40412 |  | 0.080825
Total mansion power Units |  |  | Kwh |  |  | 1330 | 6735 |  | 1347
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 8.442% | 0.42147 |  | 0.084293
Total fire & em, power Units |  |  | Kwh |  |  | 1190 | 6173 |  | 1234.6
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.554% | 0.38632 |  | 0.077265
Main Lighting & Small power pannel Sub meter
Lower Basement |  |  | KWh | 36257 | 36338 | 81
upper basement |  |  | KWh | 84066 | 84490 | 424
Level 1 |  |  | KWh | 39208 | 39414 | 206
Level 2 |  |  | KWh | 6261 | 6267 | 6
2nd floor plant room |  |  | KWh | 0 | 0 | 0
5th floor spa |  |  | KWh | 2374 | 2378 | 4
5th Floor |  |  | KWh | 154137 | 154342 | 205
12th Floor |  |  | KWh | 155406 | 155606 | 200
20th Floor |  |  | KWh | 49645 | 49895 | 250
27th Floor |  |  | KWh | 243946 | 244093 | 147
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79332 | 79402 | 70

## 6
Daily Utility Consumption Report
Prepaired by --- Devendra | 2021-05-06 | occupancy | 10% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 34 | Last year same month avg
|  | humidity | 84%
Description |  |  |  | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 5807328 | 5822905 | 15577 | 95472 | 12000 | 15912
BEST supply |  |  | KVAH | 5841454 | 5857109 | 15655 | 95865 | 12000 | 15977.5
Transformer - 1 - 2500KVA |  |  | kwh | 1068028 | 1083115 | 15087 | 92401 | -3977.5 | 15400.1667
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 15087 | 92401 | 490 | 15400.1667
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1672745 | 1673222 | 477 | 2565 | 800 | 427.5
372.5
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 0 | 0 | 320 | 65 | 53.3333
BMC |  |  | KL | 138075 | 138131 | 56 | 319 |  | 53.1667
Total water | [5 empty] | 56 | 639 | -41.5 | 106.5
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 15655 | 9 | 140895 | 862785 |  | 143797.5
C.N.G |  |  | Cu.Mtr | 477 | 49 | 23373 | 125685 |  | 20947.5
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 56 | 134 | 7504 | 42746 |  | 7124.3333
Water Tanker |  |  | KL | 0 | 80 | 0 | 25600 |  | 4266.6667
Total cost | [5 empty] | 171772 | 1056816 |  | 176136
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 897088 | 899256 | 2168 | 12797 |  | 2132.8333
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 346435 | 346755 | 320 | 2147 |  | 357.8333
Fire Emergency Power Panel - 1000A |  |  | kwh | 101398 | 102587 | 1189 | 7362 |  | 1227
Main Power Panel -1600A |  |  | kwh | 126054 | 127253 | 1199 | 7657 |  | 1276.1667
Main Lighting and Small power Panel |  |  | kwh | 255727 | 257374 | 1647 | 10721 |  | 1786.8333
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 0 | 0 | 0 | -0.23 |  | -0.038333
Chiller No 1 |  |  | kwh | 206065 | 210906 | 4841 | 29378 |  | 4896.3333
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 985171 | 987468 | 2297 | 13510 |  | 2251.6667
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 0 |  | 0
Sub Total | [5 empty] | 13661 | 83571.77 |  | 13928.6283
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732 | 260732 | 0 | -0.13 |  | -0.021667
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 479444 | 480292 | 848 | 5756 |  | 959.3333
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 419100 | 419613 | 513 | 3302 |  | 550.3333
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 11743 | 11817 | 74 | 439 |  | 73.1667
Chiller No -3 - 1200A |  |  | kwh | 346926 | 346926 | 0 | 0 |  | 0
Chiller No-4 - 1200A |  |  | Kwh | 589345 | 589355 | 10 | 66.53 |  | 11.0883
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 47133 | 47256 | 123 | 588 |  | 98
Sub Total | [5 empty] | 1568 | 10151.4 | 348 | 1691.9
|  |  | Total TR1 & TR2 |  |  | 15229 | 93723.17 | -142 | 15620.5283
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 0 | 0 | 0 | 0.002 |  | 0.00033333
5th floor spa |  |  | KWh | 2378 | 2382 | 4 | 23 |  | 3.8333
5th Floor |  |  | KWh | 154342 | 154546 | 204 | 1247 |  | 207.8333
12th Floor |  |  | KWh | 155606 | 155781 | 175 | 1182 |  | 197
20th Floor |  |  | KWh | 49895 | 50147 | 252 | 1576 |  | 262.6667
27th Floor |  |  | KWh | 244093 | 244238 | 145 | 1064 |  | 177.3333
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79402 | 79443 | 41 | 449 |  | 74.8333
Consumption of Extra AHU run |  |  | KWh
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855540 | 855571 | 31 | 110 |  | 18.3333
Main kitchen power panel no 2 |  |  | KWh | 885882 | 885883 | 1 | 7 |  | 1.1667
Prato kitchen power panel |  |  | KWh | 2373 | 2388 | 15 | 109 |  | 18.1667
San- Qi Indian Kitchen |  |  | KWh | 11231 | 11285 | 54 | 315 |  | 52.5
San- Qi Japanese Kitchen |  |  | KWh | 5979 | 6031 | 52 | 322 |  | 53.6667
The club kitchen |  |  | KWh | 701807 | 701857 | 50 | 295 |  | 49.1667
AER Kitchen |  |  | KWh | 670446 | 670495 | 49 | 470 |  | 78.3333
COLD ROOM'S |  |  | KWh | 827689 | 827846 | 157 | 1062 |  | 177
Ball Room 1 kitchen |  |  | KWh | 518572 | 518923 | 351 | 2185 |  | 364.1667
Ball Room 2 kitchen |  |  | KWh | 636838 | 636961 | 123 | 483 |  | 80.5
B1 Laundry |  |  | kwh | 107685 | 107726 | 41 | 114 |  | 19
STP Electrical |  |  | kwh | 15884 | 16098 | 214 | 1327 |  | 221.1667
Cooling Tower |  |  | kwh | 483976 | 484806 | 830 | 4673 |  | 778.8333
Total | [5 empty] | 1968 | 11472 |  | 1912
MOCK Up Room |  |  | Kwh | 459964 | 459993 | 29 | 726 |  | 121
27th Floor |  |  | Kwh | 80979 | 80997 | 18 | 78 |  | 13
Physic57 |  |  | Kwh | 152056 | 152079 | 23 | 274 |  | 45.6667
Pinoor Legal- Lighting |  |  | Kwh | 64866 | 64872 | 6 | 38 |  | 6.3333
Pinoor Legal- Lighting |  |  | Kwh | 3272 | 3272 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27918.61 | 27925 | 6.39 | 6.39 |  | 1.065
WATER
R.o.plant |  |  | KL | 244729 | 244729 | 0 | 205 |  | 34.1667
STP Water Prod |  |  | KL | 183978 | 184078 | 100 | 547 |  | 91.1667
Total water Produce |  |  |  | 0 |  | 100 | 605 |  | 100.8333
Domestic Zone-1 |  |  | KL | 413154 | 413193 | 39 | 307 |  | 51.1667
Domestic Zone-2 |  |  | KL | 102399 | 102408 | 9 | 65 |  | 10.8333
Domestic Zone-3 |  |  | KL | 97506 | 97515 | 9 | 88 |  | 14.6667
Flush Zone -1 |  |  | KL | 149560 | 149568 | 8 | 35 |  | 5.8333
Flush Zone -2 |  |  | KL | 7205 | 7207 | 2 | 22 |  | 3.6667
Flush Zone -3 |  |  | KL | 5190 | 5195 | 5 | 57 |  | 9.5
Total water consum | [5 empty] | 72 | 574 |  | 95.6667
Water Branches
Branches
Swimming pool |  |  | KL | 7435 | 7439 | 4 | 8 |  | 1.3333
B2 Laundry |  |  | KL | 35847 | 35847 | 0 | 19 |  | 3.1667
Boiler Feed Water |  |  | KL | 19635 | 19638 | 3 | 21 |  | 3.5
Total | [5 empty] | 7 | 48 |  | 8
Branches ( STP Water ) |  |  | KL |  |  |  | 0
cooling tower filling water |  |  | KL | 61439 | 61479 | 40 | 305 |  | 50.8333
STP flush(new water meter) |  |  | KL | 32267 | 32267 | 0 | 32 |  | 5.3333
Garden Water Pump |  |  | KL | 4441 | 4441 | 0 | 73 |  | 12.1667
Total | [5 empty] | 40 | 410 |  | 68.3333
Flushing Water | [6 empty] | 0 |  | 0
Flush Zone 2 pump meter |  |  | KL | 11286 | 11289 | 3 | 30 |  | 5
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8163 | 8166 | 3 | 40 |  | 6.6667
Flush Tanker |  |  | KL |  |  | 0 | 0 |  | 0
Total | [5 empty] | 6 | 70 |  | 11.6667
Total Domestic Water (R.O +BMC) |  |  | KL |  | 56 | 56 | 524 |  | 87.3333
Total Domestic Consumption |  |  | KL |  | 64 | 64 | 539 |  | 89.8333
Total STP Consumption |  |  | KL |  | 40 | 40 | 410 |  | 68.3333
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 827112 | 827318 | 206 | 1229.54 |  | 204.9233
Prato Kitchen Gas meter Reading |  |  | m3 | 73583 | 73583 | 0 | -0.4 |  | -0.066667
BallRoom Gas |  |  | m3 | 144974 | 145031 | 57 | 343.56 |  | 57.26
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970 | 8970 | 0 | 0.3 |  | 0.05
Boiler Gas Consumption | [5 empty] | 214 | 992 |  | 165.3333
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 39866 | 39890 | 24 | 143.52 |  | 23.92
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 23.56 | 0
Chiller - 3 |  |  | hr | 41385 | 41385 | 0 | 0 |  | 0
Chiller - 4 |  |  | hr | 32583 | 32582.56 | -0.44 | -0.44 |  | -0.073333
Steam Boiler -1 |  |  | hr | 22749.51 | 22749.51 | 0 | 9.92 | 11.38 | 1.6533
Steam Boiler -2 |  |  | hr | 25051.59 | 25051.59 | 0 | 0 |  | 0
Steam Boiler -3 |  |  | hr | 70324.82 | 70336.2 | 11.38 | 20.39 |  | 3.3983
Hot Water Generator -1 |  |  | hr | 1655.82 | 1663.48 | 7.66 | 46.62 | 0 | 7.77
Hot Water Generator -2 |  |  | hr | 4637 | 4637 | 0 | 0 |  | 0
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4465 | 26306.87 |  | 4384.4783
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 28.66% | 1.6536 |  | 0.2756
Total Chillers Units |  |  | kwh |  |  | 4851 | 29444.53 |  | 4907.4217
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 31.14% | 1.8506 |  | 0.30843
Total Lighting Units |  |  | kwh |  |  | 2160 | 14023 |  | 2337.1667
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 13.87% | 0.8811 |  | 0.14685
Total power Units |  |  | Kwh |  |  | 1199 | 7657 |  | 1276.1667
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.697% | 0.4811 |  | 0.080183
Total mansion power Units |  |  | Kwh |  |  | 1168 | 7903 |  | 1317.1667
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 7.498% | 0.49645 |  | 0.082741
Total fire & em, power Units |  |  | Kwh |  |  | 1189 | 7362 |  | 1227
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.633% | 0.46265 |  | 0.077109
Main Lighting & Small power pannel Sub meter
Lower Basement |  |  | KWh | 36338 | 36420 | 82
upper basement |  |  | KWh | 84490 | 84915 | 425
Level 1 |  |  | KWh | 39414 | 39622 | 208
Level 2 |  |  | KWh | 6267 | 6274 | 7
2nd floor plant room |  |  | KWh | 0 | 0 | 0
5th floor spa |  |  | KWh | 2378 | 2382 | 4
5th Floor |  |  | KWh | 154342 | 154546 | 204
12th Floor |  |  | KWh | 155606 | 155781 | 175
20th Floor |  |  | KWh | 49895 | 50147 | 252
27th Floor |  |  | KWh | 244093 | 244238 | 145
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79402 | 79443 | 41

## 7
Daily Utility Consumption Report
Prepaired by--- Devendra | 2021-05-07 | occupancy | 16% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 33 | Last year same month avg
|  | humidity | 80%
Description |  |  |  | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 5822905 | 5837836 | 14931 | 110403 | 12000 | 15771.8571
BEST supply |  |  | KVAH | 5857109 | 5872131 | 15022 | 110887 | 12000 | 15841
Transformer - 1 - 2500KVA |  |  | kwh | 1083115 | 1097539 | 14424 | 106825 | -3841 | 15260.7143
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 14424 | 106825 | 507 | 15260.7143
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1673222 | 1673570 | 348 | 2913 | 800 | 416.1429
383.8571
WATER CONSUMPTION
Tankers |  |  | KL | 0 | 0 | 0 | 320 | 65 | 45.7143
BMC |  |  | KL | 138131 | 138187 | 56 | 375 |  | 53.5714
Total water | [5 empty] | 56 | 695 | -34.2857 | 99.2857
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 15022 | 9 | 135198 | 997983 |  | 142569
C.N.G |  |  | Cu.Mtr | 348 | 51.45 | 17904.6 | 143589.6 |  | 20512.8
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 56 | 134 | 7504 | 50250 |  | 7178.5714
Water Tanker |  |  | KL | 0 | 80 | 0 | 25600 |  | 3657.1429
Total cost | [5 empty] | 160606.6 | 1217422.6 |  | 173917.5143
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 899256 | 901319 | 2063 | 14860 |  | 2122.8571
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 346755 | 347065 | 310 | 2457 |  | 351
Fire Emergency Power Panel - 1000A |  |  | kwh | 102587 | 103812 | 1225 | 8587 |  | 1226.7143
Main Power Panel -1600A |  |  | kwh | 127253 | 128365 | 1112 | 8769 |  | 1252.7143
Main Lighting and Small power Panel |  |  | kwh | 257374 | 258976 | 1602 | 12323 |  | 1760.4286
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 0 | 0 | 0 | -0.23 |  | -0.032857
Chiller No 1 |  |  | kwh | 210906 | 215512 | 4606 | 33984 |  | 4854.8571
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 987468 | 989658 | 2190 | 15700 |  | 2242.8571
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 0 |  | 0
Sub Total | [5 empty] | 13108 | 96679.77 |  | 13811.3957
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732 | 260732 | 0 | -0.13 |  | -0.018571
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 480292 | 481149 | 857 | 6613 |  | 944.7143
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 419613 | 420133 | 520 | 3822 |  | 546
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 11817 | 11889 | 72 | 511 |  | 73
Chiller No -3 - 1200A |  |  | kwh | 346926 | 346926 | 0 | 0 |  | 0
Chiller No-4 - 1200A |  |  | Kwh | 589355 | 589365 | 10 | 76.53 |  | 10.9329
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 47256 | 47256 | 0 | 588 |  | 84
Sub Total | [5 empty] | 1459 | 11610.4 | 364 | 1658.6286
|  |  | Total TR1 & TR2 |  |  | 14567 | 108290.17 | -143 | 15470.0243
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 0 | 0 | 0 | 0.002 |  | 0.00028571
5th floor spa |  |  | KWh | 2382 | 2386 | 4 | 27 |  | 3.8571
5th Floor |  |  | KWh | 154546 | 154753 | 207 | 1454 |  | 207.7143
12th Floor |  |  | KWh | 155781 | 155951 | 170 | 1352 |  | 193.1429
20th Floor |  |  | KWh | 50147 | 50396 | 249 | 1825 |  | 260.7143
27th Floor |  |  | KWh | 244238 | 244363 | 125 | 1189 |  | 169.8571
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79443 | 79477 | 34 | 483 |  | 69
Consumption of Extra AHU run |  |  | KWh
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855571 | 855573 | 2 | 112 |  | 16
Main kitchen power panel no 2 |  |  | KWh | 885883 | 885884 | 1 | 8 |  | 1.1429
Prato kitchen power panel |  |  | KWh | 2388 | 2400 | 12 | 121 |  | 17.2857
San- Qi Indian Kitchen |  |  | KWh | 11285 | 11340 | 55 | 370 |  | 52.8571
San- Qi Japanese Kitchen |  |  | KWh | 6031 | 6086 | 55 | 377 |  | 53.8571
The club kitchen |  |  | KWh | 701857 | 701907 | 50 | 345 |  | 49.2857
AER Kitchen |  |  | KWh | 670495 | 670567 | 72 | 542 |  | 77.4286
COLD ROOM'S |  |  | KWh | 827846 | 827990 | 144 | 1206 |  | 172.2857
Ball Room 1 kitchen |  |  | KWh | 518923 | 519290 | 367 | 2552 |  | 364.5714
Ball Room 2 kitchen |  |  | KWh | 636961 | 636992 | 31 | 514 |  | 73.4286
B1 Laundry |  |  | kwh | 107726 | 107745 | 19 | 133 |  | 19
STP Electrical |  |  | kwh | 16098 | 16295 | 197 | 1524 |  | 217.7143
Cooling Tower |  |  | kwh | 484806 | 485652 | 846 | 5519 |  | 788.4286
Total | [5 empty] | 1851 | 13323 |  | 1903.2857
MOCK Up Room |  |  | Kwh | 459993 | 460025 | 32 | 758 |  | 108.2857
27th Floor |  |  | Kwh | 80997 | 81025 | 28 | 106 |  | 15.1429
Physic57 |  |  | Kwh | 152079 | 152103 | 24 | 298 |  | 42.5714
Pinoor Legal- Lighting |  |  | Kwh | 64872 | 64879 | 7 | 45 |  | 6.4286
Pinoor Legal- Lighting |  |  | Kwh | 3272 | 3272 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27925 | 27927 | 2 | 8.39 |  | 1.1986
WATER
R.o.plant |  |  | KL | 244729 | 244729 | 0 | 205 |  | 29.2857
STP Water Prod |  |  | KL | 184078 | 184149 | 71 | 618 |  | 88.2857
Total water Produce |  |  |  | 0 |  | 71 | 676 |  | 96.5714
Domestic Zone-1 |  |  | KL | 413193 | 413224 | 31 | 338 |  | 48.2857
Domestic Zone-2 |  |  | KL | 102408 | 102416 | 8 | 73 |  | 10.4286
Domestic Zone-3 |  |  | KL | 97515 | 97525 | 10 | 98 |  | 14
Flush Zone -1 |  |  | KL | 149568 | 149573 | 5 | 40 |  | 5.7143
Flush Zone -2 |  |  | KL | 7207 | 7214 | 7 | 29 |  | 4.1429
Flush Zone -3 |  |  | KL | 5195 | 5205 | 10 | 67 |  | 9.5714
Total water consum | [5 empty] | 71 | 645 |  | 92.1429
Water Branches
Branches
Swimming pool |  |  | KL | 7344 | 7349 | 5 | 13 |  | 1.8571
B2 Laundry |  |  | KL | 35691 | 35697 | 6 | 25 |  | 3.5714
Boiler Feed Water |  |  | KL | 19456 | 19457 | 1 | 22 |  | 3.1429
Total | [5 empty] | 12 | 60 |  | 8.5714
Branches ( STP Water ) |  |  | KL |  |  |  | 0
cooling tower filling water |  |  | KL | 61479 | 61538 | 59 | 364 |  | 52
STP flush(new water meter) |  |  | KL | 32267 | 32267 | 0 | 32 |  | 4.5714
Garden Water Pump |  |  | KL | 4441 | 4460 | 19 | 92 |  | 13.1429
Total | [5 empty] | 78 | 488 |  | 69.7143
Flushing Water | [6 empty] | 0 |  | 0
Flush Zone 2 pump meter |  |  | KL | 11289 | 11294 | 5 | 35 |  | 5
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8166 | 8175 | 9 | 49 |  | 7
Flush Tanker |  |  | KL |  |  | 0 | 0 |  | 0
Total | [5 empty] | 14 | 84 |  | 12
Total Domestic Water (R.O +BMC) |  |  | KL |  | 56 | 56 | 580 |  | 82.8571
Total Domestic Consumption |  |  | KL |  | 66 | 66 | 605 |  | 86.4286
Total STP Consumption |  |  | KL |  | 78 | 78 | 488 |  | 69.7143
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 827318 | 827522 | 204 | 1433.54 |  | 204.7914
Prato Kitchen Gas meter Reading |  |  | m3 | 73583 | 73583 | 0 | -0.4 |  | -0.057143
BallRoom Gas |  |  | m3 | 145031 | 145102 | 71 | 414.56 |  | 59.2229
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970 | 8970 | 0 | 0.3 |  | 0.042857
Boiler Gas Consumption | [5 empty] | 73 | 1065 |  | 152.1429
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 39890 | 39913.6 | 23.6 | 167.12 |  | 23.8743
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 23.6 | 0
Chiller - 3 |  |  | hr | 41385 | 41385 | 0 | 0 |  | 0
Chiller - 4 |  |  | hr | 32582.56 | 32582.56 | 0 | -0.44 |  | -0.062857
Steam Boiler -1 |  |  | hr | 22749.51 | 22749.51 | 0 | 9.92 | 0 | 1.4171
Steam Boiler -2 |  |  | hr | 25051.59 | 25051.59 | 0 | 0 |  | 0
Steam Boiler -3 |  |  | hr | 70336.2 | 70336.2 | 0 | 20.39 |  | 2.9129
Hot Water Generator -1 |  |  | hr | 1663.48 | 1671.25 | 7.77 | 54.39 | 7.77 | 7.77
Hot Water Generator -2 |  |  | hr | 4637 | 4637 | 0 | 0 |  | 0
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4253 | 30559.87 |  | 4365.6957
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 28.48% | 1.9385 |  | 0.27692
Total Chillers Units |  |  | kwh |  |  | 4616 | 34060.53 |  | 4865.79
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 30.92% | 2.1597 |  | 0.30853
Total Lighting Units |  |  | kwh |  |  | 2122 | 16145 |  | 2306.4286
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 14.21% | 1.0232 |  | 0.14617
Total power Units |  |  | Kwh |  |  | 1112 | 8769 |  | 1252.7143
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.448% | 0.55557 |  | 0.079367
Total mansion power Units |  |  | Kwh |  |  | 1167 | 9070 |  | 1295.7143
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 7.816% | 0.57461 |  | 0.082087
Total fire & em, power Units |  |  | Kwh |  |  | 1225 | 8587 |  | 1226.7143
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 8.204% | 0.5447 |  | 0.077814
Main Lighting & Small power pannel Sub meter
Lower Basement |  |  | KWh | 36420 | 36502 | 82
upper basement |  |  | KWh | 84915 | 85326 | 411
Level 1 |  |  | KWh | 39622 | 39835 | 213
Level 2 |  |  | KWh | 6274 | 6280 | 6
2nd floor plant room |  |  | KWh | 0 | 0 | 0
5th floor spa |  |  | KWh | 2382 | 2386 | 4
5th Floor |  |  | KWh | 154546 | 154753 | 207
12th Floor |  |  | KWh | 155781 | 155951 | 170
20th Floor |  |  | KWh | 50147 | 50396 | 249
27th Floor |  |  | KWh | 244238 | 244363 | 125
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79443 | 79477 | 34

## 8
Daily Utility Consumption Report
Prepaired by---Ramesh | 2021-05-08 | occupancy | 24% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 27 | Last year same month avg
|  | humidity | 78%
Description |  |  |  | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 5837836 | 5857289 | 19453 | 129856 | 12000 | 16232 | 11335 | 8118
BEST supply |  |  | KVAH | 5872131 | 5891695 | 19564 | 130451 | 12000 | 16306.375
Transformer - 1 - 2500KVA |  |  | kwh | 1097539 | 1116375.5 | 18836.5 | 125661.5 | -4232 | 15707.6875
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal |  |  |  |  | 0 | 18836.5 | 125661.5 | 616.5 | 15707.6875
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1673570 | 1674183.48 | 613.48 | 3526.48 | 800 | 440.81
359.19
WATER CONSUMPTION
Tankers |  |  | KL | 0 | 6 | 60 | 380 | 65 | 47.5
BMC |  |  | KL | 138187 | 138242 | 55 | 430 |  | 53.75
Total water | [5 empty] | 115 | 810 | -36.25 | 101.25
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4250 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 19564 | 9 | 176076 | 1174059 |  | 146757.375
C.N.G |  |  | Cu.Mtr | 613.48 | 51.45 | 31563.546 | 175153.146 |  | 21894.1432
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 55 | 134 | 7370 | 57620 |  | 7202.5
Water Tanker |  |  | KL | 60 | 80 | 4800 | 30400 |  | 3800
Total cost | [5 empty] | 219809.546 | 1437232.146 |  | 179654.0182
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 901319 | 903746.47 | 2427.47 | 17287.47 |  | 2160.9337
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 307.125
Fire Emergency Power Panel - 1000A |  |  | kwh | 103812 | 105159.02 | 1347.02 | 9934.02 |  | 1241.7525
Main Power Panel -1600A |  |  | kwh | 128365 | 129568.27 | 1203.27 | 9972.27 |  | 1246.5338
Main Lighting and Small power Panel |  |  | kwh | 258976 | 260900.75 | 1924.75 | 14247.75 |  | 1780.9688
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 0 | 0.23 | 0.23 | 0 |  | 0
Chiller No 1 |  |  | kwh | 215512 | 220397.19 | 4885.19 | 38869.19 |  | 4858.6488
Chiller No 2- |  |  | kwh | 59200 | 59200.08 | 0.08 | 0.08 |  | 0.01
Chiller Water pump Panel- 630A |  |  | kwh | 989658 | 992083.27 | 2425.27 | 18125.27 |  | 2265.6588
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 0 |  | 0
Sub Total | [5 empty] | 14213.28 | 110893.05 |  | 13861.6313
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732 | 260732.13 | 0.13 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 481149 | 482535.31 | 1386.31 | 7999.31 |  | 999.9137
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144639.87 | -0.13 | -0.13 |  | -0.01625
Main Power Panel -1800A |  |  | kwh | 539606 | 539606.07 | 0.07 | 0.07 |  | 0.00875
Main Lighting and Small power Panel |  |  | kwh | 420133 | 420654.07 | 521.07 | 4343.07 |  | 542.8838
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 8200 | 11960.7 | 3760.7 | 4271.7 |  | 533.9625
Chiller No -3 - 1200A |  |  | kwh | 1979.37 | 1979.37 | 0 | 0 |  | 0
Chiller No-4 - 1200A |  |  | Kwh | 589365 | 589375.11 | 10.11 | 86.64 |  | 10.83
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 47256 | 47461.13 | 205.13 | 793.13 |  | 99.1412
Sub Total | [5 empty] | 5883.39 | 17493.79 | -643.67 | 2186.7237
|  |  | Total TR1 & TR2 |  |  | 20096.67 | 128386.84 | -1260.17 | 16048.355
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.002 |  | 0.00025
5th floor spa |  |  | KWh | 2386 | 2389.54 | 3.54 | 30.54 |  | 3.8175
5th Floor |  |  | KWh | 154753 | 154960.59 | 207.59 | 1661.59 |  | 207.6987
12th Floor |  |  | KWh | 155951 | 156159.2 | 208.2 | 1560.2 |  | 195.025
20th Floor |  |  | KWh | 50396 | 50673.49 | 277.49 | 2102.49 |  | 262.8112
27th Floor |  |  | KWh | 244363 | 244529.27 | 166.27 | 1355.27 |  | 169.4087
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79477 | 79618.4 | 141.4 | 624.4 |  | 78.05
Consumption of Extra AHU run |  |  | KWh |  | .
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855573 | 855588 | 15 | 127 |  | 15.875
Main kitchen power panel no 2 |  |  | KWh | 885884 | 885885 | 1 | 9 |  | 1.125
Prato kitchen power panel |  |  | KWh | 2400 | 2411.7 | 11.7 | 132.7 |  | 16.5875
San- Qi Indian Kitchen |  |  | KWh | 11340 | 11406.63 | 66.63 | 436.63 |  | 54.5787
San- Qi Japanese Kitchen |  |  | KWh | 6086 | 6140.92 | 54.92 | 431.92 |  | 53.99
The club kitchen |  |  | KWh | 701907 | 701955 | 48 | 393 |  | 49.125
AER Kitchen |  |  | KWh | 670567 | 670636 | 69 | 611 |  | 76.375
COLD ROOM'S |  |  | KWh | 827990 | 828094 | 104 | 1310 |  | 163.75
Ball Room 1 kitchen |  |  | KWh | 519290 | 519663.72 | 373.72 | 2925.72 |  | 365.715
Ball Room 2 kitchen |  |  | KWh | 636992 | 637063.8 | 71.8 | 585.8 |  | 73.225
B1 Laundry |  |  | kwh | 107745 | 107756.66 | 11.66 | 144.66 |  | 18.0825
STP Electrical |  |  | kwh | 16295 | 16451 | 156 | 1680 |  | 210
Cooling Tower |  |  | kwh | 485652 | 486446 | 794 | 6313 |  | 789.125
Total | [5 empty] | 1777.43 | 15100.43 |  | 1887.5538
MOCK Up Room |  |  | Kwh | 460025 | 460053.72 | 28.72 | 28.72 |  | 3.59
27th Floor |  |  | Kwh | 81025 | 81026.7 | 1.7 | 1.7 |  | 0.2125
Physic57 |  |  | Kwh | 152103 | 152123.95 | 20.95 | 20.95 |  | 2.6188
Pinoor Legal- Lighting |  |  | Kwh | 64879 | 64885.9 | 6.9 | 6.9 |  | 0.8625
Pinoor Legal- Lighting |  |  | Kwh | 3272 | 3272.4 | 0.4 | 0.4 |  | 0.05
20th Floor Project office |  |  |  | 27927 | 27929 | 2 | 2
WATER
R.o.plant |  |  | KL | 244729 | 244782 | 53 | 258 |  | 32.25
STP Water Prod |  |  | KL | 184149 | 184198 | 49 | 667 |  | 83.375
Total water Produce |  |  |  | 0 |  | 102 | 778 |  | 97.25
Domestic Zone-1 |  |  | KL | 413224 | 413302 | 78 | 416 |  | 52
Domestic Zone-2 |  |  | KL | 102416 | 102425 | 9 | 82 |  | 10.25
Domestic Zone-3 |  |  | KL | 97525 | 97538 | 13 | 111 |  | 13.875
Flush Zone -1 |  |  | KL | 149573 | 149587 | 14 | 54 |  | 6.75
Flush Zone -2 |  |  | KL | 7214 | 7214 | 0 | 29 |  | 3.625
Flush Zone -3 |  |  | KL | 5205 | 5212 | 7 | 74 |  | 9.25
Total water consum | [5 empty] | 121 | 766 |  | 95.75
Water Branches
Branches
Swimming pool |  |  | KL | 7349 | 7349 | 0 | 13 |  | 1.625
B2 Laundry |  |  | KL | 35697 | 35703 | 6 | 31 |  | 3.875
Boiler Feed Water |  |  | KL | 19457 | 19465 | 8 | 30 |  | 3.75
Total | [5 empty] | 14 | 74 |  | 9.25
Branches ( STP Water ) |  |  | KL |  |  |  | 0
cooling tower filling water |  |  | KL | 61538 | 61579 | 41 | 405 |  | 50.625
STP flush(new water meter) |  |  | KL | 32267 | 32279 | 12 | 44 |  | 5.5
Garden Water Pump |  |  | KL | 4460 | 4460 | 0 | 92 |  | 11.5
Total | [5 empty] | 53 | 541 |  | 67.625
Flushing Water | [6 empty] | 0 |  | 0
Flush Zone 2 pump meter |  |  | KL | 11294 | 11298 | 4 | 39 |  | 4.875
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8175 | 8179 | 4 | 53 |  | 6.625
Flush Tanker |  |  | KL |  |  | 0 | 0 |  | 0
Total | [5 empty] | 8 | 92 |  | 11.5
Total Domestic Water (R.O +BMC) |  |  | KL |  | 108 | 108 | 688 |  | 86
Total Domestic Consumption |  |  | KL |  | 107 | 107 | 712 |  | 89
Total STP Consumption |  |  | KL |  | 53 | 53 | 541 |  | 67.625
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 827522 | 827731.84 | 209.84 | 1643.38 |  | 205.4225
Prato Kitchen Gas meter Reading |  |  | m3 | 73583 | 73583.4 | 0.4 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145102 | 145179.5 | 77.5 | 492.06 |  | 61.5075
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404.2 | 0.2 | 0.2 |  | 0.025
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970 | 8970.6 | 0.6 | 0.9 |  | 0.1125
Boiler Gas Consumption | [5 empty] | 324.94
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 39913.6 | 39937.25 | 23.65 | 190.77 |  | 23.8462 | 39913.25
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 23.65 | 0
Chiller - 3 |  |  | hr | 41385 | 41393.33 | 8.33 | 8.33 |  | 1.0413
Chiller - 4 |  |  | hr | 32582.56 | 32582.56 | 0 | -0.44 |  | -0.055
Steam Boiler -1 |  |  | hr | 22749.51 | 22755.26 | 5.75 | 15.67 | 14.08 | 1.9587
Steam Boiler -2 |  |  | hr | 25051.59 | 25051.59 | 0 | 0 |  | 0
Steam Boiler -3 |  |  | hr | 70336.2 | 70338.14 | 1.94 | 22.33 | 1.94 | 2.7913
Hot Water Generator -1 |  |  | hr | 1671.25 | 1679.24 | 7.99 | 62.38 |  | 7.7975
Hot Water Generator -2 |  |  | hr | 4637 | 4636.88 | -0.12 | -0.12 |  | -0.015
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4852.87 | 35412.74 |  | 4426.5925
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 24.95% | 2.1879 |  | 0.27349
Total Chillers Units |  |  | kwh |  |  | 4895.38 | 38955.91 |  | 4869.4888
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 25.17% | 2.4114 |  | 0.30142
Total Lighting Units |  |  | kwh |  |  | 2445.82 | 18590.82 |  | 2323.8525
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 12.57% | 1.149 |  | 0.14362
Total power Units |  |  | Kwh |  |  | 1203.34 | 9972.34 |  | 1246.5425
% of power Units of Total Con.(LT) |  |  | % |  |  | 6.186% | 0.61743 |  | 0.077179
Total mansion power Units |  |  | Kwh |  |  | 1386.31 | 10456.31 |  | 1307.0387
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 7.126% | 0.64587 |  | 0.080734
Total fire & em, power Units |  |  | Kwh |  |  | 1346.89 | 9933.89 |  | 1241.7362
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 6.924% | 0.61394 |  | 0.076742
Main Lighting & Small power pannel Sub meter
Lower Basement |  |  | KWh | 36502 | 36586.2 | 84.2
upper basement |  |  | KWh | 85326 | 85741.57 | 415.57
Level 1 |  |  | KWh | 39835 | 40045.4 | 210.4
Level 2 |  |  | KWh | 6280 | 6289.63 | 9.63
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2386 | 2389.54 | 3.54
5th Floor |  |  | KWh | 154753 | 154960.59 | 207.59
12th Floor |  |  | KWh | 155951 | 156159.2 | 208.2
20th Floor |  |  | KWh | 50396 | 50673.49 | 277.49
27th Floor |  |  | KWh | 244363 | 244529.27 | 166.27
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79477 | 79618.4 | 141.4
Note on F55: Ramesh.Kadam: Previous day reading was inccorect.

## 9
Daily Utility Consumption Report
Prepaired by - Nilesh | 2021-05-09 | occupancy | 60% |  |  | Occupancy% | Electricity | Water | Gas | Occupancy%
|  | Avg temp | 29 | Last year same month avg
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day | units.consum
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 5857289 | 5872618 | 15329 | 145185 | 12000 | 16131.6667 | 11359
BEST supply |  |  | KVAH | 5891695 | 5907092 | 15397 | 145848 | 12000 | 16205.3333 | 11487
Transformer - 1 - 2500KVA |  |  | kwh | 1116375.5 | 1131200 | 14824.5 | 140486 | -4131.6667 | 15609.5556 | 11077
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0 | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0 | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0 | 0
SubTotal | [5 empty] | 14824.5 | 140486 | 504.5 | 15609.5556 | 11077
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1674183.48 | 1674707 | 523.52 | 4050 | 800 | 450 | 330.546
350
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 4 | 40 | 420 | 65 | 46.6667 | 0
BMC |  |  | KL | 138242 | 138297 | 55 | 485 |  | 53.8889 | 55
Total water | [5 empty] | 95 | 905 | -35.5556 | 100.5556 | 55
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0 | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0 | 0
Total HSD (H.S.D.) Stock |  |  | L | 4250 | 4250 | 0 | 0 |  | 0 | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 15397 | 9 | 138573 | 1312632 |  | 145848 | 114870
C.N.G |  |  | Cu.Mtr | 523.52 | 51.45 | 26935.104 | 202088.25 |  | 22454.25 | 11569.11
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0 | 0
Water BMC |  |  | Kl | 55 | 134 | 7370 | 64990 |  | 7221.1111 | 7370
Water Tanker |  |  | KL | 40 | 80 | 3200 | 33600 |  | 3733.3333 | 0
Total cost | [5 empty] | 176078.104 | 1613310.25 |  | 179256.6944 | 133809.11
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 903746.47 | 905872 | 2125.53 | 19413 |  | 2157 | 1380.84
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 273 | 514.64
Fire Emergency Power Panel - 1000A |  |  | kwh | 105159.02 | 106343 | 1183.98 | 11118 |  | 1235.3333 | 1164.46
Main Power Panel -1600A |  |  | kwh | 129568.27 | 130798 | 1229.73 | 11202 |  | 1244.6667 | 0
Main Lighting and Small power Panel |  |  | kwh | 260900.75 | 262691 | 1790.25 | 16038 |  | 1782 | 1951.13
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 0.23 | 0.23 | 0 | 0 |  | 0 | 0
Chiller No 1 |  |  | kwh | 220397.19 | 225164 | 4766.81 | 43636 |  | 4848.4444 | 2876.32
Chiller No 2- |  |  | kwh | 59200.08 | 59200 | -0.08 | 0 |  | 0 | 0
Chiller Water pump Panel- 630A |  |  | kwh | 992083.27 | 994224 | 2140.73 | 20266 |  | 2251.7778 | 1531.24
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0 | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0 | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 0 |  | 0 | 0
Sub Total | [5 empty] | 13236.95 | 124130 |  | 13792.2222 | 9418.63
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0 | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 482535.31 | 483397 | 861.69 | 8861 |  | 984.5556 | 609.49
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144639.87 | 0 | -0.13 |  | -0.014444 | 0
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0.07 |  | 0.0077778 | 1071.89
Main Lighting and Small power Panel |  |  | kwh | 420654.07 | 421167 | 512.93 | 4856 |  | 539.5556 | 85.4559
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 11960.7 | 12032 | 71.3 | 4343 |  | 482.5556 | 0
Chiller No -3 - 1200A |  |  | kwh | 1979.37 | 1979.37 | 0 | 0 |  | 0 | 0
Chiller No-4 - 1200A |  |  | Kwh | 589375.11 | 589375.11 | 0 | 86.64 |  | 9.6267 | 0
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0 | 0
B2-Loundry power panel |  |  | kwh | 47461.13 | 47473 | 11.87 | 805 |  | 89.4444 | -0.297
Sub Total | [5 empty] | 1457.79 | 18951.58 | 634.26 | 2105.7311 | 1766.5389
|  |  | Total TR1 & TR2 |  |  | 14694.74 | 143081.58 | 129.76 | 15897.9533 | 11185.1689
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.002 |  | 0.00022222 | 0
5th floor spa |  |  | KWh | 2389.54 | 2393 | 3.46 | 34 |  | 3.7778 | 0
5th Floor |  |  | KWh | 154960.59 | 155156 | 195.41 | 1857 |  | 206.3333 | 161.904
12th Floor |  |  | KWh | 156159.2 | 156346 | 186.8 | 1747 |  | 194.1111 | 215.747
20th Floor |  |  | KWh | 50673.49 | 50927 | 253.51 | 2356 |  | 261.7778 | 243.635
27th Floor |  |  | KWh | 244529.27 | 244700 | 170.73 | 1526 |  | 169.5556 | 74.992
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0 | 92.6
Sanqi |  |  | KWh | 79618.4 | 79731 | 112.6 | 737 |  | 81.8889 | 12.728
Consumption of Extra AHU run |  |  | KWh
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855588 | 855604 | 16 | 143 |  | 15.8889 | 11
Main kitchen power panel no 2 |  |  | KWh | 885885 | 885886 | 1 | 10 |  | 1.1111 | 2
Prato kitchen power panel |  |  | KWh | 2411.7 | 2422 | 10.3 | 143 |  | 15.8889 | 11
San- Qi Indian Kitchen |  |  | KWh | 11406.63 | 11458 | 51.37 | 488 |  | 54.2222 | 62
San- Qi Japanese Kitchen |  |  | KWh | 6140.92 | 6196 | 55.08 | 487 |  | 54.1111 | 4
The club kitchen |  |  | KWh | 701955 | 702003 | 48 | 441 |  | 49 | 19
AER Kitchen |  |  | KWh | 670636 | 670702 | 66 | 677 |  | 75.2222 | 31
COLD ROOM'S |  |  | KWh | 828094 | 828200 | 106 | 1416 |  | 157.3333 | 100
Ball Room 1 kitchen |  |  | KWh | 519663.72 | 520053 | 389.28 | 3315 |  | 368.3333 | 158.96
Ball Room 2 kitchen |  |  | KWh | 637063.8 | 637140 | 76.2 | 662 |  | 73.5556 | 79.2
B1 Laundry |  |  | kwh | 107756.66 | 107790 | 33.34 | 178 |  | 19.7778 | 30.15
STP Electrical |  |  | kwh | 16451 | 16683 | 232 | 1912 |  | 212.4444 | 316
Cooling Tower |  |  | kwh | 486446 | 487244 | 798 | 7111 |  | 790.1111 | 408
Total | [5 empty] | 1882.57 | 16983 |  | 1887 | 1232.31
MOCK Up Room |  |  | Kwh | 460053.72 | 460084 | 30.28 | 59 |  | 6.5556
27th Floor |  |  | Kwh | 81026.7 | 81037 | 10.3 | 12 |  | 1.3333
Physic57 |  |  | Kwh | 152123.95 | 152146 | 22.05 | 43 |  | 4.7778
Pinoor Legal- Lighting |  |  | Kwh | 64885.9 | 64892 | 6.1 | 13 |  | 1.4444
Pinoor Legal- Lighting |  |  | Kwh | 3272.4 | 3272 | -0.4 | 0 |  | 0
20th Floor Project office |  |  | kwh | 27929 | 27931 | 2
WATER
R.o.plant |  |  | KL | 244782 | 244814 | 32 | 290 |  | 32.2222 | 0
STP Water Prod |  |  | KL | 184198 | 184304 | 106 | 773 |  | 85.8889 | 71
Total water Produce |  |  |  | 0 |  | 138 | 916 |  | 101.7778 | 71
Domestic Zone-1 |  |  | KL | 413302 | 413342 | 40 | 456 |  | 50.6667 | 26
Domestic Zone-2 |  |  | KL | 102425 | 102436 | 11 | 93 |  | 10.3333 | 11
Domestic Zone-3 |  |  | KL | 97538 | 97553 | 15 | 126 |  | 14 | 9
Flush Zone -1 |  |  | KL | 149587 | 149597 | 10 | 64 |  | 7.1111 | 24
Flush Zone -2 |  |  | KL | 7214 | 7217 | 3 | 32 |  | 3.5556 | 3
Flush Zone -3 |  |  | KL | 5212 | 5215 | 3 | 77 |  | 8.5556 | 0
Total water consum | [5 empty] | 82 | 848 |  | 94.2222 | 73
Water Branches
Branches
Swimming pool |  |  | KL | 7349 | 7349 | 0 | 13 |  | 1.4444 | 0
B2 Laundry |  |  | KL | 35703 | 35860 | 157 | 188 |  | 20.8889 | 0
Boiler Feed Water |  |  | KL | 19465 | 19649 | 184 | 214 |  | 23.7778 | 4
Total | [5 empty] | 341 | 415 |  | 46.1111 | 4
Branches ( STP Water ) |  |  | KL | 0 |  |  | 0
cooling tower filling water |  |  | KL | 61579 | 61629 | 50 | 455 |  | 50.5556 | 40
STP flush(new water meter) |  |  | KL | 32279 | 32288 | 9 | 53 |  | 5.8889 | 43
Garden Water Pump |  |  | KL | 4460 | 4460 | 0 | 92 |  | 10.2222 | 0
Total | [5 empty] | 59 | 600 |  | 66.6667 | 83
Flushing Water | [6 empty] | 0 |  | 0
Flush Zone 2 pump meter |  |  | KL | 11298 | 11303 | 5 | 44 |  | 4.8889 | 5
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8179 | 8183 | 4 | 57 |  | 6.3333 | 3
Flush Tanker |  |  | KL |  |  | 0 | 0 |  | 0 | 0
Total | [5 empty] | 9 | 101 |  | 11.2222 | 8
Total Domestic Water (R.O +BMC) |  |  | KL |  | 87 | 87 | 775 |  | 86.1111 | 55
Total Domestic Consumption |  |  | KL |  | 72 | 72 | 784 |  | 87.1111 | 49
Total STP Consumption |  |  | KL |  | 59 | 59 | 600 |  | 66.6667 | 83
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 827731.84 | 827918 | 186.16 | 1829.54 |  | 203.2822 | 111.451
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0 | 0
BallRoom Gas |  |  | m3 | 145179.5 | 145242 | 62.5 | 554.56 |  | 61.6178 | 43.22
Sanqi IndianGas meter Reading |  |  | m3 | 31404.2 | 31404.2 | 0 | 0.2 |  | 0.022222 | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970.6 | 8971 | 0.4 | 1.3 |  | 0.14444 | 0
Boiler Gas Consumption | [5 empty] | 274.46 |  |  |  | 175.875
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0 | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0 | 0
Chiller - 1 |  |  | hr | 39937.25 | 39960.33 | 23.08 | 213.85 |  | 23.7611 | 22
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 23.08 | 0 | 0
Chiller - 3 |  |  | hr | 41393.33 | 41393.33 | 0 | 8.33 |  | 0.92556 | 0
Chiller - 4 |  |  | hr | 32582.56 | 32582.56 | 0 | -0.44 |  | -0.048889 | 0
Steam Boiler -1 |  |  | hr | 22755.26 | 22759 | 3.74 | 19.41 | 3.74 | 2.1567 | -0.3
Steam Boiler -2 |  |  | hr | 25051.59 | 25051.26 | -0.33 | -0.33 |  | -0.036667 | 0
Steam Boiler -3 |  |  | hr | 70338.14 | 70341.76 | 3.62 | 25.95 | 3.29 | 2.8833 | 9.71
Hot Water Generator -1 |  |  | hr | 1679.24 | 1685.98 | 6.74 | 69.12 |  | 7.68 | 0
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.013333 | 3.65
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4266.26 | 39679 |  | 4408.7778 | 2912.08
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 27.83% | 2.4663 |  | 0.27403 | 0.25637
Total Chillers Units |  |  | kwh |  |  | 4766.73 | 43722.64 |  | 4858.0711 | 2876.32
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 31.1% | 2.7223 |  | 0.30248 | 0.25322
Total Lighting Units |  |  | kwh |  |  | 2303.18 | 20894 |  | 2321.5556 | 2036.5859
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 15.02% | 1.2992 |  | 0.14436 | 0.17929
Total power Units |  |  | Kwh |  |  | 1229.73 | 11202.07 |  | 1244.6744 | 1071.89
% of power Units of Total Con.(LT) |  |  | % |  |  | 8.022% | 0.69765 |  | 0.077517 | 0.094365
Total mansion power Units |  |  | Kwh |  |  | 861.69 | 11318 |  | 1257.5556 | 1124.13
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.621% | 0.70208 |  | 0.078009 | 0.098964
Total fire & em, power Units |  |  | Kwh |  |  | 1183.98 | 11117.87 |  | 1235.3189 | 1164.46
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.724% | 0.69117 |  | 0.076797 | 0.10251
Main Lighting & Small power pannel Sub meter
Lower Basement |  |  | KWh | 36586.2 | 36665 | 78.8
upper basement |  |  | KWh | 85741.57 | 86130 | 388.43
Level 1 |  |  | KWh | 40045.4 | 40244 | 198.6
Level 2 |  |  | KWh | 6289.63 | 6310 | 20.37
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2389.54 | 2393 | 3.46
5th Floor |  |  | KWh | 154960.59 | 155156 | 195.41
12th Floor |  |  | KWh | 156159.2 | 156346 | 186.8
20th Floor |  |  | KWh | 50673.49 | 50927 | 253.51
27th Floor |  |  | KWh | 244529.27 | 244700 | 170.73
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79618.4 | 79731 | 112.6

## 10
Daily Utility Consumption Report
Prepaired by ---Nilesh | 2021-05-10 | occupancy | 52% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 30 | Last year same month avg
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 5872618 | 5887762 | 15144 | 160329 | 12000 | 16032.9
BEST supply |  |  | KVAH | 5907092 | 5922347 | 15255 | 161103 | 12000 | 16110.3
Transformer - 1 - 2500KVA |  |  | kwh | 1131200 | 1145721 | 14521 | 155007 | -4032.9 | 15500.7
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 14521 | 155007 | 623 | 15500.7
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1674707 | 1674950 | 243 | 4293 | 800 | 429.3
370.7
WATER CONSUMPTION
Tankers |  |  | KL | 4 | 2 | 20 | 440 | 65 | 44
BMC |  |  | KL | 138297 | 138354 | 57 | 542 |  | 54.2
Total water | [5 empty] | 77 | 982 | -33.2 | 98.2
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4250 | 4250 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 15255 | 9 | 137295 | 1449927 |  | 144992.7
C.N.G |  |  | Cu.Mtr | 243 | 51.45 | 12502.35 | 214590.6 |  | 21459.06
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 57 | 134 | 7638 | 72628 |  | 7262.8
Water Tanker |  |  | KL | 20 | 80 | 1600 | 35200 |  | 3520
Total cost | [5 empty] | 159035.35 | 1772345.6 |  | 177234.56
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 905872 | 907723 | 1851 | 21264 |  | 2126.4
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 245.7
Fire Emergency Power Panel - 1000A |  |  | kwh | 106343 | 107530 | 1187 | 12305 |  | 1230.5
Main Power Panel -1600A |  |  | kwh | 130798 | 131865 | 1067 | 12269 |  | 1226.9
Main Lighting and Small power Panel |  |  | kwh | 262691 | 264341 | 1650 | 17688 |  | 1768.8
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 0.23 | 0.23 | 0 | 0 |  | 0
Chiller No 1 |  |  | kwh | 225164 | 230025 | 4861 | 48497 |  | 4849.7
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 994224 | 996352 | 2128 | 22394 |  | 2239.4
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 0 |  | 0
Sub Total | [5 empty] | 12744 | 136874 |  | 13687.4
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 483397 | 484336 | 939 | 9800 |  | 980
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144639.87 | 0 | -0.13 |  | -0.013
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0.07 |  | 0.007
Main Lighting and Small power Panel |  |  | kwh | 421167 | 421690 | 523 | 5379 |  | 537.9
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12032 | 12105 | 73 | 4416 |  | 441.6
Chiller No -3 - 1200A |  |  | kwh | 1979.37 | 1979.37 | 0 | 0 |  | 0
Chiller No-4 - 1200A |  |  | Kwh | 589375.11 | 589375 | -0.11 | 86.53 |  | 8.653
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 47473 | 47522 | 49 | 854 |  | 85.4
Sub Total | [5 empty] | 1583.89 | 20535.47 | 816.11 | 2053.547
|  |  | Total TR1 & TR2 |  |  | 14327.89 | 157409.47 | 927.11 | 15740.947
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.002 |  | 0.0002
5th floor spa |  |  | KWh | 2393 | 2397 | 4 | 38 |  | 3.8
5th Floor |  |  | KWh | 155156 | 155359 | 203 | 2060 |  | 206
12th Floor |  |  | KWh | 156346 | 156480 | 134 | 1881 |  | 188.1
20th Floor |  |  | KWh | 50927 | 51186 | 259 | 2615 |  | 261.5
27th Floor |  |  | KWh | 244700 | 244826 | 126 | 1652 |  | 165.2
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79731 | 79831 | 100 | 837 |  | 83.7
Consumption of Extra AHU run |  |  | KWh
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855604 | 855621 | 17 | 160 |  | 16
Main kitchen power panel no 2 |  |  | KWh | 885886 | 885887 | 1 | 11 |  | 1.1
Prato kitchen power panel |  |  | KWh | 2422 | 2434 | 12 | 155 |  | 15.5
San- Qi Indian Kitchen |  |  | KWh | 11458 | 11511 | 53 | 541 |  | 54.1
San- Qi Japanese Kitchen |  |  | KWh | 6196 | 6253 | 57 | 544 |  | 54.4
The club kitchen |  |  | KWh | 702003 | 702055 | 52 | 493 |  | 49.3
AER Kitchen |  |  | KWh | 670702 | 670772 | 70 | 747 |  | 74.7
COLD ROOM'S |  |  | KWh | 828200 | 828309 | 109 | 1525 |  | 152.5
Ball Room 1 kitchen |  |  | KWh | 520053 | 520396 | 343 | 3658 |  | 365.8
Ball Room 2 kitchen |  |  | KWh | 637140 | 637217 | 77 | 739 |  | 73.9
B1 Laundry |  |  | kwh | 107790 | 107801 | 11 | 189 |  | 18.9
STP Electrical |  |  | kwh | 16683 | 16845 | 162 | 2074 |  | 207.4
Cooling Tower |  |  | kwh | 487244 | 487880 | 636 | 7747 |  | 774.7
Total | [5 empty] | 1600 | 18583 |  | 1858.3
MOCK Up Room |  |  | Kwh | 460084 | 460177 | 93 | 152 |  | 15.2
27th Floor |  |  | Kwh | 81037 | 81054 | 17 | 29 |  | 2.9
Physic57 |  |  | Kwh | 152146 | 152265 | 119 | 162 |  | 16.2
Pinoor Legal- Lighting |  |  | Kwh | 64892 | 64898 | 6 | 19 |  | 1.9
Pinoor Legal- Lighting |  |  | Kwh | 3272 | 3272 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27931 | 27933 | 2
WATER
R.o.plant |  |  | KL | 244814 | 244814 | 0 | 290 |  | 29
STP Water Prod |  |  | KL | 184304 | 184349 | 45 | 818 |  | 81.8
Total water Produce | [5 empty] | 45 | 961 |  | 96.1
Domestic Zone-1 |  |  | KL | 413342 | 413366 | 24 | 480 |  | 48
Domestic Zone-2 |  |  | KL | 102436 | 102443 | 7 | 100 |  | 10
Domestic Zone-3 |  |  | KL | 97553 | 97562 | 9 | 135 |  | 13.5
Flush Zone -1 |  |  | KL | 149597 | 149609 | 12 | 76 |  | 7.6
Flush Zone -2 |  |  | KL | 7217 | 7220 | 3 | 35 |  | 3.5
Flush Zone -3 |  |  | KL | 5215 | 5218 | 3 | 80 |  | 8
Total water consum | [5 empty] | 58 | 906 |  | 90.6
Water Branches
Branches
Swimming pool |  |  | KL | 7349 | 7349 | 8 | 21 |  | 2.1
B2 Laundry |  |  | KL | 35860 | 35860 | 0 | 188 |  | 18.8
Boiler Feed Water |  |  | KL | 19649 | 19650 | 1 | 215 |  | 21.5
Total | [5 empty] | 9 | 424 |  | 42.4
Branches ( STP Water ) |  |  | KL
cooling tower filling water |  |  | KL | 61629 | 61669 | 40 | 495 |  | 49.5
STP flush(new water meter) |  |  | KL | 32288 | 32299 | 11 | 64 |  | 6.4
Garden Water Pump |  |  | KL | 4460 | 4466 | 6 | 98 |  | 9.8
Total | [5 empty] | 57 | 657 |  | 65.7
Flushing Water | [6 empty] | 0 |  | 0
Flush Zone 2 pump meter |  |  | KL | 11303 | 11309 | 6 | 50 |  | 5
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8183 | 8185 | 2 | 59 |  | 5.9
Flush Tanker |  |  | KL |  |  | 0 | 0 |  | 0
Total | [5 empty] | 8 | 109 |  | 10.9
Total Domestic Water (R.O +BMC) |  |  | KL |  | 57 | 57 | 832 |  | 83.2
Total Domestic Consumption |  |  | KL |  | 46 | 46 | 830 |  | 83
Total STP Consumption |  |  | KL |  | 57 | 57 | 657 |  | 65.7
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 827918 | 828118 | 200 | 2029.54 |  | 202.954
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145242 | 145277 | 35 | 589.56 |  | 58.956
Sanqi IndianGas meter Reading |  |  | m3 | 31404.2 | 31404.2 | 0 | 0.2 |  | 0.02
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.13
Boiler Gas Consumption | [5 empty] | 8
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 39960.33 | 39984.36 | 24.03 | 237.88 |  | 23.788
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 24.03 | 0
Chiller - 3 |  |  | hr | 41393.33 | 41393.33 | 0 | 8.33 |  | 0.833
Chiller - 4 |  |  | hr | 32582.56 | 32582.56 | 0 | -0.44 |  | -0.044
Steam Boiler -1 |  |  | hr | 22759 | 22759 | 0 | 19.41 | 0 | 1.941
Steam Boiler -2 |  |  | hr | 25051.26 | 25051.26 | 0 | -0.33 |  | -0.033
Steam Boiler -3 |  |  | hr | 70341.76 | 70341.89 | 0.13 | 26.08 | 0.13 | 2.608
Hot Water Generator -1 |  |  | hr | 1685.98 | 1693.56 | 7.58 | 76.7 |  | 7.67
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.012
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 3979 | 43658 |  | 4365.8
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 26.27% | 2.729 |  | 0.2729
Total Chillers Units |  |  | kwh |  |  | 4860.89 | 48583.53 |  | 4858.353
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 32.1% | 3.0433 |  | 0.30433
Total Lighting Units |  |  | kwh |  |  | 2173 | 23067 |  | 2306.7
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 14.35% | 1.4427 |  | 0.14427
Total power Units |  |  | Kwh |  |  | 1067 | 12269.07 |  | 1226.907
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.046% | 0.76811 |  | 0.076811
Total mansion power Units |  |  | Kwh |  |  | 939 | 12257 |  | 1225.7
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 6.2% | 0.76409 |  | 0.076409
Total fire & em, power Units |  |  | Kwh |  |  | 1187 | 12304.87 |  | 1230.487
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.838% | 0.76956 |  | 0.076956
Main Lighting & Small power pannel Sub meter
Lower Basement |  |  | KWh | 36665 | 36748 | 83
upper basement |  |  | KWh | 86130 | 86560 | 430
Level 1 |  |  | KWh | 40244 | 40455 | 211
Level 2 |  |  | KWh | 6310 | 6329 | 19
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2393 | 2397 | 4
5th Floor |  |  | KWh | 155156 | 155359 | 203
12th Floor |  |  | KWh | 156346 | 156480 | 134
20th Floor |  |  | KWh | 50927 | 51186 | 259
27th Floor |  |  | KWh | 244700 | 244826 | 126
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79731 | 79831 | 100
Water Branches
Branches
Swimming pool |  |  | KL | 7010 | 7010 | 0
B2 Laundry |  |  | KL | 34070 | 34070 | 0
Boiler Feed Water |  |  | KL | 18160 | 18171 | 11
Total | [5 empty] | 11
Branches ( STP Water ) |  |  | KL
cooling tower filling water |  |  | KL | 42234 | 42285 | 51
STP flush(new water meter) |  |  | KL | 20656 | 20656 | 0
Garden Water Pump |  |  | KL | 2801 | 2801 | 0
Total | [5 empty] | 51
Flushing Water
Flush Zone 2 pump meter |  |  | KL | 6979 | 6983 | 4
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 5846 | 5849 | 3
Flush Tanker |  |  | KL |  |  | 0
Total | [5 empty] | 7
Total Domestic Water (R.O +BMC) |  |  | KL |  | 57 | 57 | #VALUE!
Total Domestic Consumption |  |  | KL |  | 47 | 47 | #VALUE!
Total STP Consumption |  |  | KL |  | 76.7 | 63 | #VALUE!

## 11
Daily Utility Consumption Report
Prepaired by-- Prakash | 2021-05-11 | occupancy | 50% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 29 | Last year same month avg
|  | humidity | 80%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 5306 | 19788.59 | 14482.59 | 174811.59 | 12000 | 15891.9627
BEST supply |  |  | KVAH | 5344 | 19957.82 | 14613.82 | 175716.82 | 12000 | 15974.2564
Transformer - 1 - 2500KVA |  |  | kwh | 1145721 | 1159720.3 | 13999.3 | 169006.3 | -3891.9627 | 15364.2091
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 13999.3 | 154485.3 | 483.29 | 14044.1182
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1674950 | 1675283.69 | 333.69 | 4626.69 | 800 | 420.6082
379.3918
WATER CONSUMPTION
Tankers |  |  | KL | 2 | 2 | 20 | 460 | 65 | 41.8182
BMC |  |  | KL | 138354 | 138409 | 55 | 597 |  | 54.2727
Total water | [5 empty] | 75 | 1057 | -31.0909 | 96.0909
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2900 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4250 | 4250 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 14613.82 | 9 | 131524.38 | 1581451.38 |  | 143768.3073
C.N.G |  |  | Cu.Mtr | 333.69 | 49 | 16350.81 | 230941.41 |  | 20994.6736
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 55 | 134 | 7370 | 79998 |  | 7272.5455
Water Tanker |  |  | KL | 20 | 80 | 1600 | 36800 |  | 3345.4545
Total cost | [5 empty] | 156845.19 | 1929190.79 |  | 175380.9809
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 907723 | 909592.23 | 1869.23 | 23133.23 |  | 2103.0209
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 223.3636
Fire Emergency Power Panel - 1000A |  |  | kwh | 107530 | 108721.5 | 1191.5 | 13496.5 |  | 1226.9545
Main Power Panel -1600A |  |  | kwh | 131865 | 132863.37 | 998.37 | 13267.37 |  | 1206.1245
Main Lighting and Small power Panel |  |  | kwh | 264341 | 265908.17 | 1567.17 | 19255.17 |  | 1750.47
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 0.23 | 86.47 | 86.24 | 86.24 |  | 7.84
Chiller No 1 |  |  | kwh | 230025 | 234819.03 | 4794.03 | 53291.03 |  | 4844.6391
Chiller No 2- |  |  | kwh | 59200 | 59200.08 | 0.08 | 0.08 |  | 0.0072727
Chiller Water pump Panel- 630A |  |  | kwh | 996352 | 998445.19 | 2093.19 | 24487.19 |  | 2226.1082
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187 | 187.49 | 0.49 | 0.49 |  | 0.044545
Sub Total | [5 empty] | 12600.3 | 149474.3 |  | 13588.5727
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 484336 | 485107.95 | 771.95 | 9632.95 |  | 875.7227
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144639.87 | 0 | -0.13 |  | -0.011818
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0.07 |  | 0.0063636
Main Lighting and Small power Panel |  |  | kwh | 421690 | 422176.23 | 486.23 | 5342.23 |  | 485.6573
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12105 | 12177.65 | 72.65 | 4415.65 |  | 401.4227
Chiller No -3 - 1200A |  |  | kwh | 1979.37 | 1979.37 | 0 | 0 |  | 0
Chiller No-4 - 1200A |  |  | Kwh | 589375 | 589405.23 | 30.23 | 116.87 |  | 10.6245
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 47522 | 47522.25 | 0.25 | 805.25 |  | 73.2045
Sub Total | [5 empty] | 1361.31 | 20312.89 | 520.98 | 1846.6264
|  |  | Total TR1 & TR2 |  |  | 13961.61 | 171371.08 | 37.69 | 15579.1891
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.002 |  | 0.00018182
5th floor spa |  |  | KWh | 2397 | 2400.8 | 3.8 | 41.8 |  | 3.8
5th Floor |  |  | KWh | 155359 | 155566.77 | 207.77 | 2267.77 |  | 206.1609
12th Floor |  |  | KWh | 156480 | 156609.13 | 129.13 | 2010.13 |  | 182.7391
20th Floor |  |  | KWh | 51186 | 51430.79 | 244.79 | 2859.79 |  | 259.9809
27th Floor |  |  | KWh | 244826 | 244943.95 | 117.95 | 1769.95 |  | 160.9045
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79831 | 79870.61 | 39.61 | 876.61 |  | 79.6918
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0 |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855621 | 855635 | 14 | 174 |  | 15.8182
Main kitchen power panel no 2 |  |  | KWh | 885887 | 885888 | 1 | 12 |  | 1.0909
Prato kitchen power panel |  |  | KWh | 2434 | 2445.75 | 11.75 | 166.75 |  | 15.1591
San- Qi Indian Kitchen |  |  | KWh | 11511 | 11561.74 | 50.74 | 591.74 |  | 53.7945
San- Qi Japanese Kitchen |  |  | KWh | 6253 | 6308.05 | 55.05 | 599.05 |  | 54.4591
The club kitchen |  |  | KWh | 702055 | 702101 | 46 | 539 |  | 49
AER Kitchen |  |  | KWh | 670772 | 670836 | 64 | 811 |  | 73.7273
COLD ROOM'S |  |  | KWh | 828309 | 828451 | 142 | 1667 |  | 151.5455
Ball Room 1 kitchen |  |  | KWh | 520396 | 520724.92 | 328.92 | 3986.92 |  | 362.4473
Ball Room 2 kitchen |  |  | KWh | 637217 | 637293 | 76 | 815 |  | 74.0909
B1 Laundry |  |  | kwh | 107801 | 107811 | 10 | 199 |  | 18.0909
STP Electrical |  |  | kwh | 16845 | 16969 | 124 | 2198 |  | 199.8182
Cooling Tower |  |  | kwh | 487880 | 488432 | 552 | 8299 |  | 754.4545
Total | [5 empty] | 1475.46 | 20058.46 |  | 1823.4964
MOCK Up Room |  |  | Kwh | 460177 | 460208 | 31 | 31 |  | 2.8182
27th Floor |  |  | Kwh | 81054 | 81069 | 15 | 15 |  | 1.3636
Physic57 |  |  | Kwh | 152265 | 152287 | 22 | 22 |  | 2
Pinoor Legal- Lighting |  |  | Kwh | 64898 | 64905.2 | 7.2 | 7.2 |  | 0.65455
Pinoor Legal- Lighting |  |  | Kwh | 3272 | 3272 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27933 | 27935.5 | 2.5 | 2.5
WATER
R.o.plant |  |  | KL | 244814 | 244814 | 0 | 290 |  | 26.3636
STP Water Prod |  |  | KL | 184349 | 184393 | 44 | 862 |  | 78.3636
Total water Produce |  |  |  | 0 |  | 44 | 1005 |  | 91.3636
Domestic Zone-1 |  |  | KL | 413366 | 413392 | 26 | 506 |  | 46
Domestic Zone-2 |  |  | KL | 102443 | 102451 | 8 | 108 |  | 9.8182
Domestic Zone-3 |  |  | KL | 97562 | 97572 | 10 | 145 |  | 13.1818
Flush Zone -1 |  |  | KL | 149609 | 149615 | 6 | 82 |  | 7.4545
Flush Zone -2 |  |  | KL | 7220 | 7226 | 6 | 41 |  | 3.7273
Flush Zone -3 |  |  | KL | 5218 | 5221 | 3 | 83 |  | 7.5455
Total water consum | [5 empty] | 59 | 965 |  | 87.7273
Water Branches
Branches
Swimming pool |  |  | KL | 7473 | 7473 | 0 | 57 |  | 5.1818
B2 Laundry |  |  | KL | 35860 | 35860 | 0 | 50 |  | 4.5455
Boiler Feed Water |  |  | KL | 19650 | 19650 | 0 | 124 |  | 11.2727
Total | [5 empty] | 0 | 189 |  | 17.1818
Branches ( STP Water ) |  |  | KL
cooling tower filling water |  |  | KL | 61669 | 61722 | 53 | 134 |  | 12.1818
STP flush(new water meter) |  |  | KL | 32299 | 32299 | 0 | 12 |  | 1.0909
Garden Water Pump |  |  | KL | 4466 | 4478 | 12 | 267 |  | 24.2727
Total | [5 empty] | 65 | 780 |  | 70.9091
Flushing Water | [8 empty] | 0
Flush Zone 2 pump meter |  |  | KL | 11309 | 11312 | 3 | 3 |  | 0.27273
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8185 | 8186 | 1 | 53 |  | 4.8182
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 8.6364
Total | [5 empty] | 4 | 76 |  | 6.9091
Total Domestic Water (R.O +BMC) |  |  | KL |  | 55 | 55 | 67 |  | 6.0909
Total Domestic Consumption |  |  | KL |  | 53 | 53 | 58 |  | 5.2727
Total STP Consumption |  |  | KL |  | 65 | 65 | 71 |  | 6.4545
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 828118 | 828321 | 203 | 2232.54 |  | 202.9582
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145277 | 145337.8 | 60.8 | 650.36 |  | 59.1236
Sanqi IndianGas meter Reading |  |  | m3 | 31404.2 | 31404.2 | 0 | 0.2 |  | 0.018182
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.11818
Boiler Gas Consumption | [5 empty] | 69.89
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 39984.36 | 40008.4 | 24.04 | 261.92 |  | 23.8109
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 24.04 | 0
Chiller - 3 |  |  | hr | 41393.33 | 41393 | -0.33 | 8 |  | 0.72727
Chiller - 4 |  |  | hr | 32582.56 | 32582.56 | 0 | -0.44 |  | -0.04
Steam Boiler -1 |  |  | hr | 22759 | 22759 | 0 | 19.41 | -0.33 | 1.7645
Steam Boiler -2 |  |  | hr | 25051.26 | 25051.723 | 0.463 | 0.133 |  | 0.012091
Steam Boiler -3 |  |  | hr | 70341.89 | 70341.89 | 0 | 26.08 | 0.463 | 2.3709
Hot Water Generator -1 |  |  | hr | 1693.56 | 1701.23 | 7.67 | 84.37 |  | 7.67
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.010909
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 3962.42 | 47620.42 |  | 4329.1291
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 27.36% | 3.0026 |  | 0.27296
Total Chillers Units |  |  | kwh |  |  | 4824.34 | 53407.87 |  | 4855.2609
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 33.31% | 3.3764 |  | 0.30695
Total Lighting Units |  |  | kwh |  |  | 2053.4 | 25120.4 |  | 2283.6727
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 14.18% | 1.5845 |  | 0.14404
Total power Units |  |  | Kwh |  |  | 998.37 | 13267.44 |  | 1206.1309
% of power Units of Total Con.(LT) |  |  | % |  |  | 6.894% | 0.83705 |  | 0.076095
Total mansion power Units |  |  | Kwh |  |  | 771.95 | 13028.95 |  | 1184.45
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.33% | 0.81739 |  | 0.074308
Total fire & em, power Units |  |  | Kwh |  |  | 1191.5 | 13496.37
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 8.227% | 0.85183 |  | 0.077439
Lower Basement |  |  | KWh | 36748 | 36828.32 | 80.32
upper basement |  |  | KWh | 86560 | 86993.28 | 433.28
Level 1 |  |  | KWh | 40455 | 40676 | 221
Level 2 |  |  | KWh | 6329 | 6341.48 | 12.48
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2397 | 2400.8 | 3.8
5th Floor |  |  | KWh | 155359 | 155566.77 | 207.77
12th Floor |  |  | KWh | 156480 | 156609.13 | 129.13
20th Floor |  |  | KWh | 51186 | 51430.79 | 244.79
27th Floor |  |  | KWh | 244826 | 244943.95 | 117.95
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79831 | 79870.61 | 39.61
1490.13

## 12
Daily Utility Consumption Report
Prepaired by- Prakash | 2021-05-12 | occupancy | 50% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 30 | Last year same month avg |  | 0% | 0 | 0 | 0
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 19788.59 | 34957.87 | 15169.28 | 189980.87 | 12000 | 15831.7392
BEST supply |  |  | KVAH | 19957.82 | 35217.71 | 15259.89 | 190976.71 | 12000 | 15914.7258
Transformer - 1 - 2500KVA |  |  | kwh | 1159720.3 | 1174391 | 14670.7 | 183677 | -3831.7392 | 15306.4167
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 14670.7 | 169156 | 498.58 | 14096.3333
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1675283.69 | 1675720.12 | 436.43 | 5063.12 | 800 | 421.9267
378.0733
WATER CONSUMPTION
Tankers |  |  | KL | 2 | 0 | 0 | 460 | 65 | 38.3333
BMC |  |  | KL | 138409 | 138461 | 52 | 649 |  | 54.0833
Total water | [5 empty] | 52 | 1109 | -27.4167 | 92.4167
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2900 | 2900 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4250 | 4250 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 15259.89 | 9 | 137339.01 | 1718790.39 |  | 143232.5325
C.N.G |  |  | Cu.Mtr | 436.43 | 49 | 21385.07 | 252326.48 |  | 21027.2067
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 52 | 134 | 6968 | 86966 |  | 7247.1667
Water Tanker |  |  | KL | 0 | 80 | 0 | 36800 |  | 3066.6667
Total cost | [5 empty] | 165692.08 | 2094882.87 |  | 174573.5725
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 909592.23 | 911455.67 | 1863.44 | 24996.67 |  | 2083.0558
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 204.75
Fire Emergency Power Panel - 1000A |  |  | kwh | 108721.5 | 109905.86 | 1184.36 | 14680.86 |  | 1223.405
Main Power Panel -1600A |  |  | kwh | 132863.37 | 134083.64 | 1220.27 | 14487.64 |  | 1207.3033
Main Lighting and Small power Panel |  |  | kwh | 265908.17 | 267578.41 | 1670.24 | 20925.41 |  | 1743.7842
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 86.47 | 150.74 | 64.27 | 150.51 |  | 12.5425
Chiller No 1 |  |  | kwh | 234819.03 | 239196.55 | 4377.52 | 57668.55 |  | 4805.7125
Chiller No 2- |  |  | kwh | 59200.08 | 59200.08 | 0 | 0.08 |  | 0.0066667
Chiller Water pump Panel- 630A |  |  | kwh | 998445.19 | 1000539.3 | 2094.11 | 26581.3 |  | 2215.1083
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Sub Total | [5 empty] | 12474.21 | 161948.51 |  | 13495.7092
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 485107.95 | 485922.35 | 814.4 | 10447.35 |  | 870.6125
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144639.87 | 0 | -0.13 |  | -0.010833
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 422176.23 | 422682.71 | 506.48 | 5848.71 |  | 487.3925
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12177.65 | 12251.05 | 73.4 | 4489.05 |  | 374.0875
Chiller No -3 - 1200A |  |  | kwh | 0 | 615.96 | 615.96 | 615.96 |  | 51.33
Chiller No-4 - 1200A |  |  | Kwh | 589405.23 | 589414.75 | 9.52 | 126.39 |  | 10.5325
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 47522.25 | 47619.96 | 97.71 | 902.96 |  | 75.2467
Sub Total | [5 empty] | 2117.47 | 22430.36 | 577.6 | 1869.1967
|  |  | Total TR1 & TR2 |  |  | 14591.68 | 185962.76 | 79.02 | 15496.8967
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.002 |  | 0.00016667
5th floor spa |  |  | KWh | 2400.8 | 2404.58 | 3.78 | 45.58 |  | 3.7983
5th Floor |  |  | KWh | 155566.77 | 155788.35 | 221.58 | 2489.35 |  | 207.4458
12th Floor |  |  | KWh | 156609.13 | 156785.48 | 176.35 | 2186.48 |  | 182.2067
20th Floor |  |  | KWh | 51430.79 | 51678.48 | 247.69 | 3107.48 |  | 258.9567
27th Floor |  |  | KWh | 244943.95 | 245062.55 | 118.6 | 1888.55 |  | 157.3792
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79870.61 | 79913.82 | 43.21 | 919.82 |  | 76.6517
Consumption of Extra AHU run |  |  | KWh |  |  | 0 | 0 |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855635 | 855644 | 9 | 183 |  | 15.25
Main kitchen power panel no 2 |  |  | KWh | 885888 | 885889 | 1 | 13 |  | 1.0833
Prato kitchen power panel |  |  | KWh | 2445.75 | 2455.73 | 9.98 | 176.73 |  | 14.7275
San- Qi Indian Kitchen |  |  | KWh | 11561.74 | 11612.47 | 50.73 | 642.47 |  | 53.5392
San- Qi Japanese Kitchen |  |  | KWh | 6308.05 | 6359.46 | 51.41 | 650.46 |  | 54.205
The club kitchen |  |  | KWh | 702101 | 702150 | 49 | 588 |  | 49
AER Kitchen |  |  | KWh | 670836 | 670901 | 65 | 876 |  | 73
COLD ROOM'S |  |  | KWh | 828451 | 828563 | 112 | 1779 |  | 148.25
Ball Room 1 kitchen |  |  | KWh | 520724.92 | 521040.04 | 315.12 | 4302.04 |  | 358.5033
Ball Room 2 kitchen |  |  | KWh | 637293 | 637367.96 | 74.96 | 889.96 |  | 74.1633
B1 Laundry |  |  | kwh | 107811 | 107848.52 | 37.52 | 236.52 |  | 19.71
STP Electrical |  |  | kwh | 16969 | 17191 | 222 | 2420 |  | 201.6667
Cooling Tower |  |  | kwh | 488432 | 488984 | 552 | 8851 |  | 737.5833
Total | [5 empty] | 1549.72 | 21608.18 |  | 1800.6817
MOCK Up Room |  |  | Kwh | 460208 | 460238.84 | 30.84 | 30.84 |  | 2.57
27th Floor |  |  | Kwh | 81069 | 81080 | 11 | 11 |  | 0.91667
Physic57 |  |  | Kwh | 152287 | 152368.91 | 81.91 | 81.91 |  | 6.8258
Pinoor Legal- Lighting |  |  | Kwh | 64905.2 | 64911.6 | 6.4 | 6.4 |  | 0.53333
Pinoor Legal- Lighting |  |  | Kwh | 3272 | 3272.5 | 0.5 | 0.5 |  | 0.041667
20th Floor Project office |  |  |  | 27935.5 | 27938.45 | 2.95 | 2.95
WATER
R.o.plant |  |  | KL | 244814 | 244834 | 20 | 310 |  | 25.8333
STP Water Prod |  |  | KL | 184393 | 184512 | 119 | 981 |  | 81.75
Total water Produce |  |  |  | 0 |  | 139 | 1144 |  | 95.3333
Domestic Zone-1 |  |  | KL | 413392 | 413427 | 35 | 541 |  | 45.0833
Domestic Zone-2 |  |  | KL | 102451 | 102457 | 6 | 114 |  | 9.5
Domestic Zone-3 |  |  | KL | 97572 | 97581 | 9 | 154 |  | 12.8333
Flush Zone -1 |  |  | KL | 149615 | 149642 | 27 | 109 |  | 9.0833
Flush Zone -2 |  |  | KL | 7226 | 7227 | 1 | 42 |  | 3.5
Flush Zone -3 |  |  | KL | 5221 | 5224 | 3 | 86 |  | 7.1667
Total water consum | [5 empty] | 81 | 1046 |  | 87.1667
Water Branches
Branches
Swimming pool |  |  | KL | 7473 | 7473 | 0 | 57 |  | 4.75
B2 Laundry |  |  | KL | 35860 | 35860 | 0 | 50 |  | 4.1667
Boiler Feed Water |  |  | KL | 19650 | 19655 | 5 | 129 |  | 10.75
Total | [5 empty] | 5 | 194 |  | 16.1667
Branches ( STP Water ) |  |  | KL
cooling tower filling water |  |  | KL | 61722 | 61770 | 48 | 129 |  | 10.75
STP flush(new water meter) |  |  | KL | 32299 | 32324 | 25 | 37 |  | 3.0833
Garden Water Pump |  |  | KL | 4478 | 4478 | 0 | 255 |  | 21.25
Total | [5 empty] | 73 | 788 |  | 65.6667
Flushing Water | [8 empty] | 0
Flush Zone 2 pump meter |  |  | KL | 11312 | 11318 | 6 | 6 |  | 0.5
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8186 | 8190 | 4 | 56 |  | 4.6667
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 7.9167
Total | [5 empty] | 10 | 82 |  | 6.8333
Total Domestic Water (R.O +BMC) |  |  | KL |  | 72 | 72 | 84 |  | 7
Total Domestic Consumption |  |  | KL |  | 54 | 54 | 59 |  | 4.9167
Total STP Consumption |  |  | KL |  | 73 | 73 | 79 |  | 6.5833
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 828321 | 828521.9 | 200.9 | 2433.44 |  | 202.7867
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583 | -0.4 | -0.4 |  | -0.033333
BallRoom Gas |  |  | m3 | 145337.8 | 145389.46 | 51.66 | 702.02 |  | 58.5017
Sanqi IndianGas meter Reading |  |  | m3 | 31404.2 | 31404.2 | 0 | 0.2 |  | 0.016667
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.10833
Boiler Gas Consumption | [5 empty] | 184.27 | 1926.56
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40008.4 | 40029.35 | 20.95 | 282.87 |  | 23.5725
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 20.95 | 0
Chiller - 3 |  |  | hr | 41393 | 41396.43 | 3.43 | 11.43 |  | 0.9525
Chiller - 4 |  |  | hr | 32582.56 | 32582.56 | 0 | -0.44 |  | -0.036667
Steam Boiler -1 |  |  | hr | 22759 | 22759 | 0 | 19.41 | 3.43 | 1.6175
Steam Boiler -2 |  |  | hr | 25051.723 | 25051.72 | -0.003 | 0.13 |  | 0.010833
Steam Boiler -3 |  |  | hr | 70341.89 | 70351.94 | 10.05 | 36.13 | 10.047 | 3.0108
Hot Water Generator -1 |  |  | hr | 1701.23 | 1708.75 | 7.52 | 91.89 |  | 7.6575
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.01
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 3957.55 | 51577.97 |  | 4298.1642
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 26.09% | 3.2635 |  | 0.27196
Total Chillers Units |  |  | kwh |  |  | 5003 | 58410.87 |  | 4867.5725
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 32.98% | 3.7062 |  | 0.30885
Total Lighting Units |  |  | kwh |  |  | 2176.72 | 27297.12 |  | 2274.76
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 14.35% | 1.728 |  | 0.144
Total power Units |  |  | Kwh |  |  | 1220.27 | 14487.71 |  | 1207.3092
% of power Units of Total Con.(LT) |  |  | % |  |  | 8.044% | 0.91749 |  | 0.076457
Total mansion power Units |  |  | Kwh |  |  | 814.4 | 13843.35 |  | 1153.6125
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.369% | 0.87108 |  | 0.07259
Total fire & em, power Units |  |  | Kwh |  |  | 1184.36 | 14680.73 |  | 1223.3942
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.808% | 0.9299 |  | 0.077492
Lower Basement |  |  | KWh | 36828.32 | 36910.02 | 81.7
upper basement |  |  | KWh | 86993.28 | 87413 | 419.72
Level 1 |  |  | KWh | 40676 | 40921.15 | 245.15
Level 2 |  |  | KWh | 6341.48 | 6355.48 | 14
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2400.8 | 2404.58 | 3.78
5th Floor |  |  | KWh | 155566.77 | 155788.35 | 221.58
12th Floor |  |  | KWh | 156609.13 | 156785.48 | 176.35
20th Floor |  |  | KWh | 51430.79 | 51678.48 | 247.69
27th Floor |  |  | KWh | 244943.95 | 245062.55 | 118.6
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79870.61 | 79913.82 | 43.21
1571.78

## 13
Daily Utility Consumption Report
Prepaired by--Prakash | 2021-05-13 | occupancy | 50% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 29 | Last year same month avg
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 34957.87 | 49523.83 | 14565.96 | 204546.83 | 12000 | 15734.3715 | 0.99284 | 49723.83
BEST supply |  |  | KVAH | 35217.71 | 49888.73 | 14671.02 | 205647.73 | 12000 | 15819.0562 |  | 50088.73
Transformer - 1 - 2500KVA |  |  | kwh | 1174391 | 1188471.3 | 14080.3 | 197757.3 | -3734.3715 | 15212.1
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 14080.3 | 183236.3 | 485.66 | 14095.1
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1675720.12 | 1676371 | 650.88 | 5714 | 800 | 439.5385
360.4615
WATER CONSUMPTION
Tankers |  |  | KL | 0 | 2 | 20 | 480 | 65 | 36.9231
BMC |  |  | KL | 138461 | 138518 | 57 | 706 |  | 54.3077
Total water | [5 empty] | 77 | 1186 | -26.2308 | 91.2308
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2900 | 2900 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4250 | 4250 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 14671.02 | 9 | 132039.18 | 1850829.57 |  | 142371.5054
C.N.G |  |  | Cu.Mtr | 650.88 | 49 | 31893.12 | 284219.6 |  | 21863.0462
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 57 | 134 | 7638 | 94604 |  | 7277.2308
Water Tanker |  |  | KL | 20 | 80 | 1600 | 38400
Total cost | [5 empty] | 173170.3 | 2268053.17 |  | 174465.6285
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 911455.67 | 913250.23 | 1794.56 | 26791.23 |  | 2060.8638
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 189
Fire Emergency Power Panel - 1000A |  |  | kwh | 109905.86 | 111072 | 1166.14 | 15847 |  | 1219
Main Power Panel -1600A |  |  | kwh | 134083.64 | 135231.86 | 1148.22 | 15635.86 |  | 1202.7585
Main Lighting and Small power Panel |  |  | kwh | 267578.41 | 269227.59 | 1649.18 | 22574.59 |  | 1736.5069
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 150.74 | 210.03 | 59.29 | 209.8 |  | 16.1385
Chiller No 1 |  |  | kwh | 239196.55 | 239196.55 | 0 | 57668.55 |  | 4436.0423
Chiller No 2- |  |  | kwh | 59200.08 | 59200.08 | 0 | 0.08 |  | 0.0061538
Chiller Water pump Panel- 630A |  |  | kwh | 1000539.3 | 1002550.3 | 2011 | 28592.3 |  | 2199.4077
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187.49 | 187.49 | 0 | 0 |  | 0
Sub Total |  |  |  |  | . | 7828.39 | 169776.9 |  | 13059.7615
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 485922.35 | 486743.15 | 820.8 | 11268.15 |  | 866.7808
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144639.87 | 0 | -0.13 |  | -0.01
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 422682.71 | 423100.15 | 417.44 | 6266.15 |  | 482.0115
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12251.05 | 12326.21 | 75.16 | 4564.21 |  | 351.0931
Chiller No -3 - 1200A |  |  | kwh | 615.96 | 5227.1 | 4611.14 | 5227.1 |  | 402.0846
Chiller No-4 - 1200A |  |  | Kwh | 589414.75 | 589424.71 | 9.96 | 136.35 |  | 10.4885
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711.33 | 0.33 | 0.33 |  | 0.025385
B2-Loundry power panel |  |  | kwh | 47619.96 | 47868.12 | 248.16 | 1151.12 |  | 88.5477
Sub Total | [5 empty] | 6182.99 | 28613.35 | 554.58 | 2201.0269
|  |  | Total TR1 & TR2 |  |  | 14011.38 | 199974.14 | 68.92 | 15382.6262
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419.18 | 0.18 | 0.182 |  | 0.014
5th floor spa |  |  | KWh | 2404.58 | 2408.36 | 3.78 | 49.36 |  | 3.7969
5th Floor |  |  | KWh | 155788.35 | 155994.29 | 205.94 | 2695.29 |  | 207.33
12th Floor |  |  | KWh | 156785.48 | 156935.52 | 150.04 | 2336.52 |  | 179.7323
20th Floor |  |  | KWh | 51678.48 | 51922.93 | 244.45 | 3351.93 |  | 257.8408
27th Floor |  |  | KWh | 245062.55 | 245187.61 | 125.06 | 2013.61 |  | 154.8931
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79913.82 | 79957.27 | 43.45 | 963.27 |  | 74.0977
Consumption of Extra AHU run |  |  | KWh | 0 | 0 | 0 | 0 |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855644 | 855655 | 11 | 194 |  | 14.9231
Main kitchen power panel no 2 |  |  | KWh | 885889 | 885890 | 1 | 14 |  | 1.0769
Prato kitchen power panel |  |  | KWh | 2455.73 | 2464.54 | 8.81 | 185.54 |  | 14.2723
San- Qi Indian Kitchen |  |  | KWh | 11612.47 | 11663.63 | 51.16 | 693.63 |  | 53.3562
San- Qi Japanese Kitchen |  |  | KWh | 6359.46 | 6410.58 | 51.12 | 701.58 |  | 53.9677
The club kitchen |  |  | KWh | 702150 | 702188 | 38 | 626 |  | 48.1538
AER Kitchen |  |  | KWh | 670901 | 670977 | 76 | 952 |  | 73.2308
COLD ROOM'S |  |  | KWh | 828563 | 828683 | 120 | 1899 |  | 146.0769
Ball Room 1 kitchen |  |  | KWh | 521040.04 | 521360 | 319.96 | 4622 |  | 355.5385
Ball Room 2 kitchen |  |  | KWh | 637367.96 | 637438 | 70.04 | 960 |  | 73.8462
B1 Laundry |  |  | kwh | 107848.52 | 107859 | 10.48 | 247 |  | 19
STP Electrical |  |  | kwh | 17191 | 17360 | 169 | 2589 |  | 199.1538
Cooling Tower |  |  | kwh | 488984 | 489535 | 551 | 9402 |  | 723.2308
Total | [5 empty] | 1477.57 | 23085.75 |  | 1775.8269
MOCK Up Room |  |  | Kwh | 460238.84 | 460310 | 71.16 | 71.16 |  | 5.4738
27th Floor |  |  | Kwh | 81080 | 81090 | 10 | 10 |  | 0.76923
Physic57 |  |  | Kwh | 152368.91 | 152389.63 | 20.72 | 20.72 |  | 1.5938
Pinoor Legal- Lighting |  |  | Kwh | 64911.6 | 64917.8 | 6.2 | 6.2 |  | 0.47692
Pinoor Legal- Lighting |  |  | Kwh | 3272.5 | 3272.5 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27938.45 | 27942.83 | 4.38 | 4.38
WATER
R.o.plant |  |  | KL | 244834 | 244864 | 30 | 340 |  | 26.1538
STP Water Prod |  |  | KL | 184512 | 184579 | 67 | 1048 |  | 80.6154
Total water Produce |  |  |  | 0 |  | 97 | 1241 |  | 95.4615
Domestic Zone-1 |  |  | KL | 413427 | 413479 | 52 | 593 |  | 45.6154
Domestic Zone-2 |  |  | KL | 102457 | 102463 | 6 | 120 |  | 9.2308
Domestic Zone-3 |  |  | KL | 97581 | 97593 | 12 | 166 |  | 12.7692
Flush Zone -1 |  |  | KL | 149642 | 149669 | 27 | 136 |  | 10.4615
Flush Zone -2 |  |  | KL | 7227 | 7233 | 6 | 48 |  | 3.6923
Flush Zone -3 |  |  | KL | 5224 | 5228 | 4 | 90 |  | 6.9231
Total water consum | [5 empty] | 107 | 1153 |  | 88.6923
Water Branches
Branches
Swimming pool |  |  | KL | 7473 | 7473 | 0 | 57 |  | 4.3846
B2 Laundry |  |  | KL | 35860 | 35875 | 15 | 65 |  | 5
Boiler Feed Water |  |  | KL | 19655 | 19660 | 5 | 129 |  | 9.9231
Total | [5 empty] | 20 | 209 |  | 16.0769
Branches ( STP Water ) |  |  | KL
cooling tower filling water |  |  | KL | 61770 | 61830 | 60 | 141 |  | 10.8462
STP flush(new water meter) |  |  | KL | 32324 | 32354 | 30 | 42 |  | 3.2308
Garden Water Pump |  |  | KL | 4478 | 4492 | 14 | 269 |  | 20.6923
Total | [5 empty] | 104 | 819 |  | 63
Flushing Water | [8 empty] | 0
Flush Zone 2 pump meter |  |  | KL | 11318 | 11326 | 8 | 8 |  | 0.61538
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8190 | 8194 | 4 | 56 |  | 4.3077
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 7.3077
Total | [5 empty] | 12 | 84 |  | 6.4615
Total Domestic Water (R.O +BMC) |  |  | KL |  | 87 | 87 | 99 |  | 7.6154
Total Domestic Consumption |  |  | KL |  | 80 | 80 | 85 |  | 6.5385
Total STP Consumption |  |  | KL |  | 104 | 104 | 110 |  | 8.4615
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 828521.9 | 828726.78 | 204.88 | 2638.32 |  | 202.9477
Prato Kitchen Gas meter Reading |  |  | m3 | 73583 | 73583 | 0 | -0.4 |  | -0.030769
BallRoom Gas |  |  | m3 | 145389.46 | 145442.09 | 52.63 | 754.65 |  | 58.05
Sanqi IndianGas meter Reading |  |  | m3 | 31404.2 | 31404 | -0.2 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.1
Boiler Gas Consumption | [5 empty] | 393.57
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40029.35 | 40029.35 | 0 | 282.87 |  | 21.7592
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41396.43 | 41420.9 | 24.47 | 35.9 |  | 2.7615
Chiller - 4 |  |  | hr | 32582.56 | 32582.56 | 0 | -0.44 |  | -0.033846
Steam Boiler -1 |  |  | hr | 22759 | 22766.92 | 7.92 | 27.33 | 32.39 | 2.1023
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 0.13 |  | 0.01
Steam Boiler -3 |  |  | hr | 70351.94 | 70351.94 | 0 | 36.13 | 0 | 2.7792
Hot Water Generator -1 |  |  | hr | 1708.75 | 1716.31 | 7.56 | 99.45 |  | 7.65
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0092308
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 3805.89 | 55383.86 |  | 4260.2969
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 26.13% | 3.5248 |  | 0.27114
Total Chillers Units |  |  | kwh |  |  | 4621.1 | 63031.97 |  | 4848.6131
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 31.73% | 4.0235 |  | 0.3095
Total Lighting Units |  |  | kwh |  |  | 2066.62 | 29363.74 |  | 2258.7492
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 14.19% | 1.8698 |  | 0.14383
Total power Units |  |  | Kwh |  |  | 1148.22 | 15635.93 |  | 1202.7638
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.883% | 0.99632 |  | 0.07664
Total mansion power Units |  |  | Kwh |  |  | 820.8 | 14664.15 |  | 1128.0115
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.635% | 0.92743 |  | 0.071341
Total fire & em, power Units |  |  | Kwh |  |  | 1166.14 | 15846.87 |  | 1218.99
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 8.006% | 1.01 |  | 0.077689
Lower Basement |  |  | KWh | 36910.02 | 36991.79 | 81.77
upper basement |  |  | KWh | 87413 | 87811.65 | 398.65
Level 1 |  |  | KWh | 40921.15 | 41174.32 | 253.17
Level 2 |  |  | KWh | 6355.48 | 6367.18 | 11.7
2nd floor plant room |  |  | KWh | 20419 | 20419.18 | 0.18
5th floor spa |  |  | KWh | 2404.58 | 2408.36 | 3.78
5th Floor |  |  | KWh | 155788.35 | 155994.29 | 205.94
12th Floor |  |  | KWh | 156785.48 | 156935.52 | 150.04
20th Floor |  |  | KWh | 51678.48 | 51922.93 | 244.45
27th Floor |  |  | KWh | 245062.55 | 245187.61 | 125.06
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79913.82 | 79957.27 | 43.45
1518.19

## 14
Daily Utility Consumption Report
Prepaired by- Prakash | 2021-05-14 | occupancy | 63% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 30 | Last year same month avg
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 49523.83 | 63827.51 | 14303.68 | 218850.51 | 12000 | 15632.1793
BEST supply |  |  | KVAH | 49888.73 | 64319.28 | 14430.55 | 220078.28 | 12000 | 15719.8771
Transformer - 1 - 2500KVA |  |  | kwh | 1188471.3 | 1202298.2 | 13826.9 | 211584.2 | -3632.1793 | 15113.1571
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0 | . | 0
SubTotal | [5 empty] | 13826.9 | 197063.2 | 476.78 | 14075.9429
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1676371 | 1676663.58 | 292.58 | 6006.58 | 800 | 429.0414
370.9586
WATER CONSUMPTION
Tankers |  |  | KL | 2 | 2 | 20 | 500 | 65 | 35.7143
BMC |  |  | KL | 138518 | 138575 | 57 | 763 |  | 54.5
Total water | [5 empty] | 77 | 1263 | -25.2143 | 90.2143
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2900 | 2900 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4250 | 4250 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 14430.55 | 9 | 129874.95 | 1980704.52 |  | 141478.8943
C.N.G |  |  | Cu.Mtr | 292.58 | 49 | 14336.42 | 298556.02 |  | 21325.43
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 57 | 134 | 7638 | 102242 |  | 7303
Water Tanker |  |  | KL | 20 | 80 | 1600 | 40000 |  | 2857.1429
Total cost | [5 empty] | 153449.37 | 2421502.54 |  | 172964.4671
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 913250.23 | 915038.95 | 1788.72 | 28579.95 |  | 2041.425 |  | .
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 175.5 |  | .++……………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………….............................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................................
Fire Emergency Power Panel - 1000A |  |  | kwh | 111072 | 112266.91 | 1194.91 | 17041.91 |  | 1217.2793
Main Power Panel -1600A |  |  | kwh | 135231.86 | 136320.97 | 1089.11 | 16724.97 |  | 1194.6407
Main Lighting and Small power Panel |  |  | kwh | 269227.59 | 271010.89 | 1783.3 | 24357.89 |  | 1739.8493
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 210.03 | 263.03 | 53 | 262.8 |  | 18.7714
Chiller No 1 |  |  | kwh | 239196.55 | 239196.55 | 0 | 57668.55 |  | 4119.1821
Chiller No 2- |  |  | kwh | 59200.08 | 59200.08 | 0 | 0.08 |  | 0.0057143
Chiller Water pump Panel- 630A |  |  | kwh | 1002550.3 | 1004558.2 | 2007.9 | 30600.2 |  | 2185.7286
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Sub Total | [5 empty] | 7916.94 | 177693.84 |  | 12692.4171
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 486743.15 | 487528.99 | 785.84 | 12053.99 |  | 860.9993
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144639.87 | 0 | -0.13 |  | -0.0092857
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 423100.15 | 423524.29 | 424.14 | 6690.29 |  | 477.8779
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12326.21 | 12398.01 | 71.8 | 4636.01 |  | 331.1436
Chiller No -3 - 1200A |  |  | kwh | 5227.1 | 9724.99 | 4497.89 | 9724.99 |  | 694.6421
Chiller No-4 - 1200A |  |  | Kwh | 589424.71 | 589424.71 | 0 | 136.35 |  | 9.7393
Chiller Water pump Panel- 630A |  |  | kwh | 7711.33 | 7711.33 | 0 | 0.33 |  | 0.023571
B2-Loundry power panel |  |  | kwh | 47868.12 | 47868.27 | 0.15 | 1151.27 |  | 82.2336
Sub Total | [5 empty] | 5779.82 | 34393.17 | 606.92 | 2456.655
|  |  | Total TR1 & TR2 |  |  | 13696.76 | 213670.9 | 130.14 | 15262.2071
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 0 | 0 | 0 | 0.182 |  | 0.013
5th floor spa |  |  | KWh | 2408.36 | 2412.15 | 3.79 | 53.15 |  | 3.7964
5th Floor |  |  | KWh | 155994.29 | 156201.05 | 206.76 | 2902.05 |  | 207.2893
12th Floor |  |  | KWh | 156935.52 | 157101.17 | 165.65 | 2502.17 |  | 178.7264
20th Floor |  |  | KWh | 51922.93 | 52175.54 | 252.61 | 3604.54 |  | 257.4671
27th Floor |  |  | KWh | 245187.61 | 245401.59 | 213.98 | 2227.59 |  | 159.1136
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 79957.27 | 80000.07 | 42.8 | 1006.07 |  | 71.8621
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855655 | 855665 | 10 | 193 |  | 13.7857
Main kitchen power panel no 2 |  |  | KWh | 885890 | 885891 | 1 | 195 |  | 13.9286
Prato kitchen power panel |  |  | KWh | 2464.54 | 2473.16 | 8.62 | 194.16 |  | 13.8686
San- Qi Indian Kitchen |  |  | KWh | 11663.63 | 11714.59 | 50.96 | 744.59 |  | 53.185
San- Qi Japanese Kitchen |  |  | KWh | 6410.58 | 6464.57 | 53.99 | 747.62 |  | 53.4014
The club kitchen |  |  | KWh | 702188 | 702211 | 23 | 649 |  | 46.3571
AER Kitchen |  |  | KWh | 670977 | 671123 | 146 | 1098 |  | 78.4286
COLD ROOM'S |  |  | KWh | 828683 | 828805 | 122 | 1074 |  | 76.7143
Ball Room 1 kitchen |  |  | KWh | 521360 | 521713.32 | 353.32 | 2252.32 |  | 160.88
Ball Room 2 kitchen |  |  | KWh | 637438 | 637518.84 | 80.84 | 1040.84 |  | 74.3457
B1 Laundry |  |  | kwh | 107859 | 107871.05 | 12.05 | 259.05 |  | 18.5036
STP Electrical |  |  | kwh | 17360 | 17536 | 176 | 2765 |  | 197.5
Cooling Tower |  |  | kwh | 489535 | 490097 | 562 | 9964 |  | 711.7143
Total | [5 empty] | 1599.78 | 24685.53 |  | 1763.2521
MOCK Up Room |  |  | Kwh | 460310 | 460333.4 | 23.4 | 23.4 |  | 1.6714
27th Floor |  |  | Kwh | 81090 | 81097.8 | 7.8 | 7.8 |  | 0.55714
Physic57 |  |  | Kwh | 152389.63 | 152441 | 51.37 | 51.37 |  | 3.6693
Pinoor Legal- Lighting |  |  | Kwh | 64917.8 | 64924.5 | 6.7 | 6.7 |  | 0.47857
Pinoor Legal- Lighting |  |  | Kwh | 3272.5 | 3272.5 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27942.83 | 27949.93 | 7.1 | 7.1
WATER
R.o.plant |  |  | KL | 244864 | 244879 | 15 | 355 |  | 25.3571
STP Water Prod |  |  | KL | 184579 | 184662 | 83 | 1131 |  | 80.7857
Total water Produce |  |  |  | 0 |  | 98 | 1339 |  | 95.6429
Domestic Zone-1 |  |  | KL | 413479 | 413525 | 46 | 639 |  | 45.6429
Domestic Zone-2 |  |  | KL | 102463 | 102473 | 10 | 130 |  | 9.2857
Domestic Zone-3 |  |  | KL | 97593 | 97610 | 17 | 183 |  | 13.0714
Flush Zone -1 |  |  | KL | 149669 | 149695 | 26 | 162 |  | 11.5714
Flush Zone -2 |  |  | KL | 7233 | 7238 | 5 | 53 |  | 3.7857
Flush Zone -3 |  |  | KL | 5228 | 5232 | 4 | 94 |  | 6.7143
Total water consum | [5 empty] | 108 | 1261 |  | 90.0714
Water Branches
Branches
Swimming pool |  |  | KL | 7473 | 7473 | 0 | 57 |  | 4.0714
B2 Laundry |  |  | KL | 35875 | 35875 | 0 | 50 |  | 3.5714
Boiler Feed Water |  |  | KL | 19660 | 19660 | 0 | 124 |  | 8.8571
Total |  |  |  | 0 |  | 0 | 189 |  | 13.5
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 61830 | 61870 | 40 | 121 |  | 8.6429
STP flush(new water meter) |  |  | KL | 32354 | 32371 | 17 | 29 |  | 2.0714
Garden Water Pump |  |  | KL | 4492 | 4492 | 0 | 255 |  | 18.2143
Total |  |  |  | 0 |  | 57 | 772 |  | 55.1429
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11326 | 11332 | 6 | 6 |  | 0.42857
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8194 | 8198 | 4 | 56 |  | 4
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 6.7857
Total | [5 empty] | 10 | 82 |  | 5.8571
Total Domestic Water (R.O +BMC) |  |  | KL |  |  | 72 | 84 |  | 6
Total Domestic Consumption |  |  | KL |  | 82 | 82 | 87 |  | 6.2143
Total STP Consumption |  |  | KL |  | 57 | 57 | 63 |  | 4.5
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 828726.78 | 828928.09 | 201.31 | 2839.63 |  | 202.8307
Prato Kitchen Gas meter Reading |  |  | m3 | 73583 | 73583 | 0 | -0.4 |  | -0.028571
BallRoom Gas |  |  | m3 | 145442.09 | 145491 | 48.91 | 803.56 |  | 57.3971
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.092857
Boiler Gas Consumption | [5 empty] | 42.36
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40029.35 | 40029.35 | 0 | 282.87 |  | 20.205
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41420.9 | 41445.13 | 24.23 | 60.13 |  | 4.295
Chiller - 4 |  |  | hr | 32582.56 | 32582.98 | 0.42 | -0.02 |  | -0.0014286
Steam Boiler -1 |  |  | hr | 22766.92 | 22766.92 | 0 | 27.33 | 24.65 | 1.9521
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 0.13 |  | 0.0092857
Steam Boiler -3 |  |  | hr | 70351.94 | 70351.94 | 0 | 36.13 | 0 | 2.5807
Hot Water Generator -1 |  |  | hr | 1716.31 | 1723.89 | 7.58 | 107.03 |  | 7.645
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0085714
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 3796.62 | 59180.48 |  | 4227.1771
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 26.54% | 3.7902 |  | 0.27073
Total Chillers Units |  |  | kwh |  |  | 4497.89 | 67529.86 |  | 4823.5614
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 31.45% | 4.3379 |  | 0.30985
Total Lighting Units |  |  | kwh |  |  | 2207.44 | 31571.18 |  | 2255.0843
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 15.43% | 2.0242 |  | 0.14458
Total power Units |  |  | Kwh |  |  | 1089.11 | 16725.04 |  | 1194.6457
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.614% | 1.0725 |  | 0.076604
Total mansion power Units |  |  | Kwh |  |  | 785.84 | 15449.99 |  | 1103.5707
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.494% | 0.98237 |  | 0.070169
Total fire & em, power Units |  |  | Kwh |  |  | 1194.91 | 17041.78 |  | 1217.27
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 8.354% | 1.0935 |  | 0.078107
Lower Basement |  |  | KWh | 36991.79 | 37071.87 | 80.08
upper basement |  |  | KWh | 87811.65 | 88224.68 | 413.03
Level 1 |  |  | KWh | 41174.32 | 41418.35 | 244.03
Level 2 |  |  | KWh | 6367.18 | 6378.14 | 10.96
2nd floor plant room |  |  | KWh | 0 | 0 | 0
5th floor spa |  |  | KWh | 2408.36 | 2412.15 | 3.79
5th Floor |  |  | KWh | 155994.29 | 156201.05 | 206.76
12th Floor |  |  | KWh | 156935.52 | 157101.17 | 165.65
20th Floor |  |  | KWh | 51922.93 | 52175.54 | 252.61
27th Floor |  |  | KWh | 245187.61 | 245401.59 | 213.98
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 79957.27 | 80000.07 | 42.8
1633.69

## 15
Daily Utility Consumption Report
Prepaired by- Nilesh | 2021-05-15 | occupancy | 83% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 31 | Last year same month avg
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 63827.51 | 80860 | 17032.49 | 235883 | 12000 | 15725.5333
BEST supply |  |  | KVAH | 64319.28 | 81436 | 17116.72 | 237195 | 12000 | 15813
Transformer - 1 - 2500KVA |  |  | kwh | 1202298.2 | 1218784 | 16485.8 | 228070 | -3725.5333 | 15204.6667
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 16485.8 | 213549 | 546.69 | 14236.6
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1676663.58 | 1677101 | 437.42 | 6444 | 800 | 429.6
370.4
WATER CONSUMPTION
Tankers |  |  | KL | 2 | 6 | 60 | 560 | 65 | 37.3333
BMC |  |  | KL | 138575 | 138631 | 56 | 819 |  | 54.6
Total water | [5 empty] | 116 | 1379 | -26.9333 | 91.9333
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2900 | 2900 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4250 | 4250 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 17116.72 | 9 | 154050.48 | 2134755 |  | 142317
C.N.G |  |  | Cu.Mtr | 437.42 | 51.45 | 22505.259 | 321061.279 |  | 21404.0853
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 56 | 134 | 7504 | 109746 |  | 7316.4
Water Tanker |  |  | KL | 60 | 80 | 4800 | 44800
Total cost | [5 empty] | 188859.739 | 2610362.279 |  | 174024.1519
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 915038.95 | 917046 | 2007.05 | 30587 |  | 2039.1333
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 163.8
Fire Emergency Power Panel - 1000A |  |  | kwh | 112266.91 | 113564 | 1297.09 | 18339 |  | 1222.6
Main Power Panel -1600A |  |  | kwh | 136320.97 | 137637 | 1316.03 | 18041 |  | 1202.7333
Main Lighting and Small power Panel |  |  | kwh | 271010.89 | 273184 | 2173.11 | 26531 |  | 1768.7333
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 263.03 | 298 | 34.97 | 297.77 |  | 19.8513
Chiller No 1 |  |  | kwh | 239196.55 | 239668 | 471.45 | 58140 |  | 3876
Chiller No 2- |  |  | kwh | 59200.08 | 59200 | -0.08 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 1004558.2 | 1006633 | 2074.8 | 32675 |  | 2178.3333
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187.49 | 187.49 | 0 | 0 |  | 0
Sub Total | [5 empty] | 9374.42 | 187068.26 |  | 12471.2173
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732 | -0.13 | -0.13 |  | -0.0086667 | 260974.13
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 487528.99 | 488424 | 895.01 | 12949 |  | 863.2667
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144639.87 | 0 | -0.13 |  | -0.0086667
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606 | -0.07 | -0.07 |  | -0.0046667
Main Lighting and Small power Panel |  |  | kwh | 423524.29 | 423999 | 474.71 | 7165 |  | 477.6667
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12398.01 | 12469 | 70.99 | 4707 |  | 313.8
Chiller No -3 - 1200A |  |  | kwh | 9724.99 | 15098 | 5373.01 | 15098 |  | 1006.5333
Chiller No-4 - 1200A |  |  | Kwh | 589424.71 | 589435.47 | 10.76 | 147.11 |  | 9.8073
Chiller Water pump Panel- 630A |  |  | kwh | 7711.33 | 7711.33 | 0 | 0.33 |  | 0.022
B2-Loundry power panel |  |  | kwh | 47868.27 | 47905 | 36.73 | 1188 |  | 79.2
Sub Total | [5 empty] | 6861.01 | 41254.18 | 797.06 | 2750.2787
|  |  | Total TR1 & TR2 |  |  | 16235.43 | 229906.33 | 250.37 | 15327.0887
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419.18 | 0.18 | 0.362 |  | 0.024133
5th floor spa |  |  | KWh | 2412.15 | 2415 | 2.85 | 56 |  | 3.7333
5th Floor |  |  | KWh | 156201.05 | 156403 | 201.95 | 3104 |  | 206.9333
12th Floor |  |  | KWh | 157101.17 | 157372 | 270.83 | 2773 |  | 184.8667
20th Floor |  |  | KWh | 52175.54 | 52447 | 271.46 | 3876 |  | 258.4
27th Floor |  |  | KWh | 245401.59 | 245741 | 339.41 | 2567 |  | 171.1333
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 80000.07 | 80090 | 89.93 | 1096 |  | 73.0667
Consumption of Extra AHU run |  |  | KWh
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855665 | 855675 | 10 | 203 |  | 13.5333
Main kitchen power panel no 2 |  |  | KWh | 885891 | 885892 | 1 | 196 |  | 13.0667
Prato kitchen power panel |  |  | KWh | 2473.16 | 2480 | 6.84 | 201 |  | 13.4
San- Qi Indian Kitchen |  |  | KWh | 11714.59 | 11767 | 52.41 | 797 |  | 53.1333
San- Qi Japanese Kitchen |  |  | KWh | 6464.57 | 6522 | 57.43 | 805.05 |  | 53.67
The club kitchen |  |  | KWh | 702211 | 702236 | 25 | 674 |  | 44.9333
AER Kitchen |  |  | KWh | 671123 | 671267 | 144 | 1242 |  | 82.8
COLD ROOM'S |  |  | KWh | 828805 | 828930 | 125 | 1199 |  | 79.9333
Ball Room 1 kitchen |  |  | KWh | 521713.32 | 522087 | 373.68 | 2626 |  | 175.0667
Ball Room 2 kitchen |  |  | KWh | 637518.84 | 637594 | 75.16 | 1116 |  | 74.4
B1 Laundry |  |  | kwh | 107871.05 | 107909 | 37.95 | 297 |  | 19.8
STP Electrical |  |  | kwh | 17536 | 17788 | 252 | 3017 |  | 201.1333
Cooling Tower |  |  | kwh | 490097 | 490696 | 599 | 10563 |  | 704.2
Total | [5 empty] | 1759.47 | 26445 |  | 1763
MOCK Up Room |  |  | Kwh | 460333.4 | 460414 | 80.6 | 80.6 |  | 5.3733
27th Floor |  |  | Kwh | 81097.8 | 81105 | 7.2 | 7.2 |  | 0.48
Physic57 |  |  | Kwh | 152441 | 152445 | 4 | 4 |  | 0.26667
Pinoor Legal- Lighting |  |  | Kwh | 64924.5 | 64930 | 5.5 | 5.5 |  | 0.36667
Pinoor Legal- Lighting |  |  | Kwh | 3272.5 | 3272.5 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27949.93 | 27954 | 4.07 | 4.07
WATER
R.o.plant |  |  | KL | 244879 | 245032 | 153 | 508 |  | 33.8667
STP Water Prod |  |  | KL | 184662 | 184793 | 131 | 1262 |  | 84.1333
Total water Produce | [5 empty] | 284 | 1623 |  | 108.2
Domestic Zone-1 |  |  | KL | 413525 | 413567 | 42 | 681 |  | 45.4
Domestic Zone-2 |  |  | KL | 102473 | 102483 | 10 | 140 |  | 9.3333
Domestic Zone-3 |  |  | KL | 97610 | 97643 | 33 | 216 |  | 14.4
Flush Zone -1 |  |  | KL | 149695 | 149718 | 23 | 185 |  | 12.3333
Flush Zone -2 |  |  | KL | 7238 | 7243 | 5 | 58 |  | 3.8667
Flush Zone -3 |  |  | KL | 5232 | 5237 | 5 | 99 |  | 6.6
Total water consum | [5 empty] | 118 | 1379 |  | 91.9333
Water Branches | [8 empty] | 3
Branches
Swimming pool |  |  | KL | 7473 | 7473 | 0 | 57 |  | 3.8
B2 Laundry |  |  | KL | 35875 | 35875 | 0 | 50 |  | 3.3333
Boiler Feed Water |  |  | KL | 19660 | 19663 | 3 | 127 |  | 8.4667
Total |  |  |  | 0 |  | 3 | 192 |  | 12.8
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 61870 | 61912 | 42 | 123 |  | 8.2
STP flush(new water meter) |  |  | KL | 32371 | 32401 | 30 | 42 |  | 2.8
Garden Water Pump |  |  | KL | 4492 | 4509 | 17 | 272 |  | 18.1333
Total |  |  |  | 0 |  | 89 | 804 |  | 53.6
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11332 | 11339 | 7 | 7 |  | 0.46667
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8198 | 8199 | 1 | 53 |  | 3.5333
Flush Tanker |  |  | KL | 0 | 0 | 0 | 95 |  | 6.3333
Total | [5 empty] | 8 | 80 |  | 5.3333
Total Domestic Water (R.O +BMC) |  |  | KL |  | 209 | 209 | 221 |  | 14.7333
Total Domestic Consumption |  |  | KL |  | 95 | 95 | 100 |  | 6.6667
Total STP Consumption |  |  | KL |  | 89 | 89 | 95 |  | 6.3333
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 828928.09 | 829129 | 200.91 | 3040.54 |  | 202.7027
Prato Kitchen Gas meter Reading |  |  | m3 | 73583 | 73583.4 | 0.4 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145491 | 145536 | 45 | 848.56 |  | 56.5707
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.086667
Boiler Gas Consumption | [5 empty] | 191.11
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40029.35 | 40031.52 | 2.17 | 285.04 |  | 19.0027
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 2.17 | 0
Chiller - 3 |  |  | hr | 41445.13 | 41469.06 | 23.93 | 84.06 |  | 5.604
Chiller - 4 |  |  | hr | 32582.98 | 32582.98 | 0 | -0.02 |  | -0.0013333
Steam Boiler -1 |  |  | hr | 22766.92 | 22766.92 | 0 | 27.33 | 23.93 | 1.822
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 0.13 |  | 0.0086667
Steam Boiler -3 |  |  | hr | 70351.94 | 70361.47 | 9.53 | 45.66 | 9.53 | 3.044
Hot Water Generator -1 |  |  | hr | 1723.89 | 1731.51 | 7.62 | 114.65 |  | 7.6433
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.008
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4081.72 | 63262.2 |  | 4217.48
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 23.96% | 4.0298 |  | 0.26866
Total Chillers Units |  |  | kwh |  |  | 5855.14 | 73385 |  | 4892.3333
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 34.38% | 4.6817 |  | 0.31211
Total Lighting Units |  |  | kwh |  |  | 2647.82 | 34219 |  | 2281.2667
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 15.55% | 2.1796 |  | 0.14531
Total power Units |  |  | Kwh |  |  | 1315.96 | 18041 |  | 1202.7333
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.726% | 1.1497 |  | 0.076648
Total mansion power Units |  |  | Kwh |  |  | 895.01 | 16345 |  | 1089.6667
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.255% | 1.0349 |  | 0.068994
Total fire & em, power Units |  |  | Kwh |  |  | 1297.09 | 18338.87 |  | 1222.5913
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.615% | 1.1697 |  | 0.077977
Lower Basement |  |  | KWh | 37071.87 | 37152.94 | 81.07
upper basement |  |  | KWh | 88224.68 | 88619 | 394.32
Level 1 |  |  | KWh | 41418.35 | 41655 | 236.65
Level 2 |  |  | KWh | 6378.14 | 6389 | 10.86
2nd floor plant room |  |  | KWh | 20419 | 20419.18 | 0.18
5th floor spa |  |  | KWh | 2412.15 | 2415 | 2.85
5th Floor |  |  | KWh | 156201.05 | 156403 | 201.95
12th Floor |  |  | KWh | 157101.17 | 157372 | 270.83
20th Floor |  |  | KWh | 52175.54 | 52447 | 271.46
27th Floor |  |  | KWh | 245401.59 | 245741 | 339.41
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 80000.07 | 80090 | 89.93
1899.51

## 16
Daily Utility Consumption Report
Prepaired by Nilesh | 2021-05-16 | occupancy | 52% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 30 | Last year same month avg
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 80860 | 95882 | 15022 | 250905 | 12000 | 15681.5625 | 5631551
BEST supply |  |  | KVAH | 81436 | 96591 | 15155 | 252350 | 12000 | 15771.875 | 5664653
Transformer - 1 - 2500KVA |  |  | kwh | 1218784 | 1233310 | 14526 | 242596 | -3681.5625 | 15162.25 | -242596
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0 |  | 15155
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 14526 | 228075 | 496 | 14254.6875
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1677101 | 1677418 | 317 | 6761 | 800 | 422.5625
377.4375
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 6 | 60 | 620 | 65 | 38.75
BMC |  |  | KL | 138631 | 138688 | 57 | 876 |  | 54.75
Total water | [5 empty] | 117 | 1496 | -28.5 | 93.5
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2900 | 2900 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4250 | 4250 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 15155 | 9 | 136395 | 2271150 |  | 141946.875
C.N.G |  |  | Cu.Mtr | 317 | 51.45 | 16309.65 | 337370.929 |  | 21085.6831
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 57 | 134 | 7638 | 117384 |  | 7336.5
Water Tanker |  |  | KL | 60 | 80 | 4800 | 49600
Total cost | [5 empty] | 165142.65 | 2775504.929 |  | 173469.0581
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 917046 | 918972 | 1926 | 32513 |  | 2032.0625
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 153.5625
Fire Emergency Power Panel - 1000A |  |  | kwh | 113564 | 114803 | 1239 | 19578 |  | 1223.625
Main Power Panel -1600A |  |  | kwh | 137637 | 138734 | 1097 | 19138 |  | 1196.125
Main Lighting and Small power Panel |  |  | kwh | 273184 | 275338 | 2154 | 28685 |  | 1792.8125
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 298 | 350 | 52 | 349.77 |  | 21.8606
Chiller No 1 |  |  | kwh | 239668 | 239668 | 0 | 58140 |  | 3633.75
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 1006633 | 1008759 | 2126 | 34801 |  | 2175.0625
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187.49 | 187.49 | 0 | 0 |  | 0
Sub Total | [5 empty] | 8594 | 195662.26 |  | 12228.8913
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732 | 260732.13 | 0.13 | 0 |  | 0 | 260976
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 488424 | 489245 | 821 | 13770 |  | 860.625
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144639.87 | 0 | -0.13 |  | -0.008125
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | -0.07 |  | -0.004375
Main Lighting and Small power Panel |  |  | kwh | 423999 | 424453 | 454 | 7619 |  | 476.1875
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12469 | 12542 | 73 | 4780 |  | 298.75
Chiller No -3 - 1200A |  |  | kwh | 15098 | 19546 | 4448 | 19546 |  | 1221.625
Chiller No-4 - 1200A |  |  | Kwh | 589435.47 | 589435.47 | 0 | 147.11 |  | 9.1944
Chiller Water pump Panel- 630A |  |  | kwh | 7711.33 | 7711.33 | 0 | 0.33 |  | 0.020625
B2-Loundry power panel |  |  | kwh | 47905 | 47905 | 0 | 1188 |  | 74.25
Sub Total | [5 empty] | 5796.13 | 47050.31 | 631.87 | 2940.6444
|  |  | Total TR1 & TR2 |  |  | 14390.13 | 244296.46 | 135.87 | 15268.5287
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419.18 | 20419.18 | 0 | 0.362 |  | 0.022625
5th floor spa |  |  | KWh | 2415 | 2419 | 4 | 60 |  | 3.75
5th Floor |  |  | KWh | 156403 | 156604 | 201 | 3305 |  | 206.5625
12th Floor |  |  | KWh | 157372 | 157667 | 295 | 3068 |  | 191.75
20th Floor |  |  | KWh | 52447 | 52707 | 260 | 4136 |  | 258.5
27th Floor |  |  | KWh | 245741 | 246073 | 332 | 2899 |  | 181.1875
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 80090 | 80185 | 95 | 1191 |  | 74.4375
Consumption of Extra AHU run |  |  | KWh
Main kitchen power panel no 1 |  |  | KWh | 855675 | 855682 | 7 | 210 |  | 13.125
Main kitchen power panel no 2 |  |  | KWh | 885892 | 885892 | 0 | 196 |  | 12.25
Prato kitchen power panel |  |  | KWh | 2480 | 2489 | 9 | 210 |  | 13.125
San- Qi Indian Kitchen |  |  | KWh | 11767 | 11821 | 54 | 851 |  | 53.1875
San- Qi Japanese Kitchen |  |  | KWh | 6522 | 6578 | 56 | 861.05 |  | 53.8156
The club kitchen |  |  | KWh | 702236 | 702265 | 29 | 703 |  | 43.9375
AER Kitchen |  |  | KWh | 671267 | 671385 | 118 | 1360 |  | 85
COLD ROOM'S |  |  | KWh | 828930 | 829050 | 120 | 1319 |  | 82.4375
Ball Room 1 kitchen |  |  | KWh | 522087 | 522420 | 333 | 2959 |  | 184.9375
Ball Room 2 kitchen |  |  | KWh | 637594 | 637676 | 82 | 1198 |  | 74.875
B1 Laundry |  |  | kwh | 107909 | 107919 | 10 | 307 |  | 19.1875
STP Electrical |  |  | kwh | 17788 | 17904 | 116 | 3133 |  | 195.8125
Cooling Tower |  |  | kwh | 490696 | 491207 | 511 | 11074 |  | 692.125
Total | [5 empty] | 1445 | 27890 |  | 1743.125
MOCK Up Room |  |  | Kwh | 460414 | 460442 | 28 | 28 |  | 1.75
27th Floor |  |  | Kwh | 81105 | 81109 | 4 | 4 |  | 0.25
Physic57 |  |  | Kwh | 152445 | 152454 | 9 | 9 |  | 0.5625
Pinoor Legal- Lighting |  |  | Kwh | 64930 | 64937 | 7 | 7 |  | 0.4375
Pinoor Legal- Lighting |  |  | Kwh | 3272.5 | 3272.5 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27954 | 27954 | 0 | 0
WATER
R.o.plant |  |  | KL | 245032 | 245077 | 45 | 553 |  | 34.5625
STP Water Prod |  |  | KL | 184793 | 184822 | 29 | 1291 |  | 80.6875
Total water Produce |  |  |  | 0 | 0 | 74 | 1697 |  | 106.0625
Domestic Zone-1 |  |  | KL | 413567 | 413594 | 27 | 708 |  | 44.25
Domestic Zone-2 |  |  | KL | 102483 | 102497 | 14 | 154 |  | 9.625
Domestic Zone-3 |  |  | KL | 97643 | 97662 | 19 | 235 |  | 14.6875 |  | 96617
Flush Zone -1 |  |  | KL | 149718 | 149723 | 5 | 190 |  | 11.875
Flush Zone -2 |  |  | KL | 7243 | 7267 | 24 | 82 |  | 5.125
Flush Zone -3 |  |  | KL | 5237 | 5247 | 10 | 109 |  | 6.8125
Total water consum | [5 empty] | 99 | 1478 |  | 92.375
Water Branches
Branches
Swimming pool |  |  | KL | 7473 | 7473 | 0 | 57 |  | 3.5625
B2 Laundry |  |  | KL | 35875 | 35875 | 0 | 50 |  | 3.125
Boiler Feed Water |  |  | KL | 19663 | 19663 | 0 | 124 |  | 7.75
Total |  |  |  | 0 |  | 0 | 189 |  | 11.8125
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 61912 | 62019 | 107 | 188 |  | 11.75
STP flush(new water meter) |  |  | KL | 32401 | 32401 | 0 | 12 |  | 0.75
Garden Water Pump |  |  | KL | 4509 | 4509 | 0 | 255 |  | 15.9375
Total |  |  |  | 0 |  | 107 | 822 |  | 51.375
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11339 | 11367 | 28 | 28 |  | 1.75
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8199 | 8206 | 7 | 59 |  | 3.6875
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 5.9375
Total | [5 empty] | 35 | 107 |  | 6.6875
Total Domestic Water (R.O +BMC) |  |  | KL |  | 102 | 102 | 114 |  | 7.125
Total Domestic Consumption |  |  | KL |  | 94 | 94 | 99 |  | 6.1875
Total STP Consumption |  |  | KL |  | 107 | 107 | 113 |  | 7.0625
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 829129 | 829338 | 209 | 3249.54 |  | 203.0963
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145536 | 145593 | 57 | 905.56 |  | 56.5975
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.08125
Boiler Gas Consumption | [5 empty] | 51 | 51 |  | 3.1875
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40031.52 | 40031.52 | 0 | 285.04 |  | 17.815
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41469.06 | 41492.65 | 23.59 | 107.65 |  | 6.7281
Chiller - 4 |  |  | hr | 32582.98 | 32582.98 | 0 | -0.02 |  | -0.00125
Steam Boiler -1 |  |  | hr | 22766.92 | 22766.92 | 0 | 27.33 | 23.59 | 1.7081
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 0.13 |  | 0.008125
Steam Boiler -3 |  |  | hr | 70361.47 | 70361.47 | 0 | 45.66 | 0 | 2.8538
Hot Water Generator -1 |  |  | hr | 1731.51 | 1739.48 | 7.97 | 122.62 |  | 7.6638
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0075
Percentage of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4052.13 | 67314.33 |  | 4207.1456
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 26.97% | 4.2996 |  | 0.26872
Total Chillers Units |  |  | kwh |  |  | 4448 | 77833 |  | 4864.5625
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 29.61% | 4.9778 |  | 0.31111
Total Lighting Units |  |  | kwh |  |  | 2608 | 36827 |  | 2301.6875
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 17.36% | 2.3532 |  | 0.14708
Total power Units |  |  | Kwh |  |  | 1097 | 19138 |  | 1196.125
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.303% | 1.2227 |  | 0.076422
Total mansion power Units |  |  | Kwh |  |  | 821 | 17166 |  | 1072.875
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.465% | 1.0896 |  | 0.068098
Total fire & em, power Units |  |  | Kwh |  |  | 1239 | 19577.87 |  | 1223.6169
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 8.248% | 1.2521 |  | 0.078258
Lower Basement |  |  | KWh | 37152.94 | 37232 | 79.06
upper basement |  |  | KWh | 88619 | 89007 | 388
Level 1 |  |  | KWh | 41655 | 41864 | 209
Level 2 |  |  | KWh | 6389 | 6402 | 13
2nd floor plant room |  |  | KWh | 20419.18 | 20419.18 | 0
5th floor spa |  |  | KWh | 2415 | 2419 | 4
5th Floor |  |  | KWh | 156403 | 156604 | 201
12th Floor |  |  | KWh | 157372 | 157667 | 295
20th Floor |  |  | KWh | 52447 | 52707 | 260
27th Floor |  |  | KWh | 245741 | 246073 | 332
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 80090 | 80185 | 95
1876.06

## 17
Daily Utility Consumption Report
Prepaired by- Nilesh | 2021-05-17 | occupancy | 60% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 29 | Last year same month avg
|  | humidity | 80%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 95882 | 110754 | 14872 | 265777 | 12000 | 15633.9412
BEST supply |  |  | KVAH | 96591 | 111639 | 15048 | 267398 | 12000 | 15729.2941
Transformer - 1 - 2500KVA |  |  | kwh | 1233310 | 1247690 | 14380 | 256976 | -3633.9412 | 15116.2353
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0 |  | 14182
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 14380 | 242455 | 492 | 14262.0588
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1677418 | 1677980 | 562 | 7323 | 800 | 430.7647
369.2353
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 2 | 20 | 640 | 65 | 37.6471
BMC |  |  | KL | 138688 | 138744 | 56 | 932 |  | 54.8235
Total water | [5 empty] | 76 | 1572 | -27.4706 | 92.4706
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2900 | 2900 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4250 | 4250 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 15048 | 9 | 135432 | 2406582 |  | 141563.6471
C.N.G |  |  | Cu.Mtr | 562 | 51.45 | 28914.9 | 366285.829 |  | 21546.2252
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 56 | 134 | 7504 | 124888 |  | 7346.3529
Water Tanker |  |  | KL | 20 | 80 | 1600 | 51200 |  |  | 16
Total cost | [5 empty] | 173450.9 | 2948955.829 |  | 173467.9899
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 918972 | 920574 | 1602 | 34115 |  | 2006.7647
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 144.5294
Fire Emergency Power Panel - 1000A |  |  | kwh | 114803 | 116141 | 1338 | 20916 |  | 1230.3529
Main Power Panel -1600A |  |  | kwh | 138734 | 139784 | 1050 | 20188 |  | 1187.5294
Main Lighting and Small power Panel |  |  | kwh | 275338 | 277493 | 2155 | 30840 |  | 1814.1176
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 350 | 430 | 80 | 429.77 |  | 25.2806
Chiller No 1 |  |  | kwh | 239668 | 239668 | 0 | 58140 |  | 3420
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 1008759 | 1010795 | 2036 | 36837 |  | 2166.8824
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187.49 | 187.49 | 0 | 0 |  | 0
Sub Total | [5 empty] | 8261 | 203923.26 |  | 11995.4859
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0 | 260974.13
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 489245 | 490007 | 762 | 14532 |  | 854.8235
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144640 | 0.13 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | -0.07 |  | -0.0041176
Main Lighting and Small power Panel |  |  | kwh | 424453 | 424944 | 491 | 8110 |  | 477.0588
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12542 | 12622 | 80 | 4860 |  | 285.8824
Chiller No -3 - 1200A |  |  | kwh | 19546 | 24040 | 4494 | 24040 |  | 1414.1176
Chiller No-4 - 1200A |  |  | Kwh | 589435.47 | 589435.47 | 0 | 147.11 |  | 8.6535
Chiller Water pump Panel- 630A |  |  | kwh | 7711.33 | 7711.33 | 0 | 0.33 |  | 0.019412
B2-Loundry power panel |  |  | kwh | 47905 | 48104 | 199 | 1387 |  | 81.5882
Sub Total | [5 empty] | 6026.13 | 53076.44 | 584.87 | 3122.1435
|  |  | Total TR1 & TR2 |  |  | 14287.13 | 258583.59 | 92.87 | 15210.7994
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419.18 | 20419 | -0.18 | 0.182 |  | 0.010706
5th floor spa |  |  | KWh | 2419 | 2423 | 4 | 64 |  | 3.7647
5th Floor |  |  | KWh | 156604 | 156870 | 266 | 3571 |  | 210.0588
12th Floor |  |  | KWh | 157667 | 157951 | 284 | 3352 |  | 197.1765
20th Floor |  |  | KWh | 52707 | 52979 | 272 | 4408 |  | 259.2941
27th Floor |  |  | KWh | 246073 | 246395 | 322 | 3221 |  | 189.4706
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 80185 | 80272 | 87 | 1278 |  | 75.1765
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
855695
Main kitchen power panel no 1 |  |  | KWh | 855682 | 855696 | 14 | 224 |  | 13.1765
Main kitchen power panel no 2 |  |  | KWh | 885892 | 885893 | 1 | 197 |  | 11.5882
Prato kitchen power panel |  |  | KWh | 2489 | 2495 | 6 | 216 |  | 12.7059
San- Qi Indian Kitchen |  |  | KWh | 11821 | 11880 | 59 | 910 |  | 53.5294
San- Qi Japanese Kitchen |  |  | KWh | 6578 | 6635 | 57 | 918.05 |  | 54.0029
The club kitchen |  |  | KWh | 702265 | 702294 | 29 | 732 |  | 43.0588
AER Kitchen |  |  | KWh | 671385 | 671474 | 89 | 1449 |  | 85.2353
COLD ROOM'S |  |  | KWh | 829050 | 829167 | 117 | 1436 |  | 84.4706
Ball Room 1 kitchen |  |  | KWh | 522420 | 522731 | 311 | 3270 |  | 192.3529
Ball Room 2 kitchen |  |  | KWh | 637676 | 637752 | 76 | 1274 |  | 74.9412
B1 Laundry |  |  | kwh | 107919 | 107930 | 11 | 318 |  | 18.7059
STP Electrical |  |  | kwh | 17904 | 18079 | 175 | 3308 |  | 194.5882
Cooling Tower |  |  | kwh | 491207 | 491626 | 419 | 11493 |  | 676.0588
Total | [5 empty] | 1364 | 29254 |  | 1720.8235
MOCK Up Room |  |  | Kwh | 460442 | 460478 | 36 | 36 |  | 2.1176
27th Floor |  |  | Kwh | 81109 | 81116 | 7 | 7 |  | 0.41176
Physic57 |  |  | Kwh | 152454 | 152520 | 66 | 66 |  | 3.8824
Pinoor Legal- Lighting |  |  | Kwh | 64937 | 64943 | 6 | 6 |  | 0.35294
Pinoor Legal- Lighting |  |  | Kwh | 3272.5 | 3272.5 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27954 | 27957 | 3 | 3
WATER |  |  |  |  | .
R.o.plant |  |  | KL | 245077 | 245077 | 0 | 553 |  | 32.5294
STP Water Prod |  |  | KL | 184822 | 184915 | 93 | 1384 |  | 81.4118
Total water Produce |  |  |  | 0 |  | 93 | 1790 |  | 105.2941
Domestic Zone-1 |  |  | KL | 413594 | 413639 | 45 | 753 |  | 44.2941
Domestic Zone-2 |  |  | KL | 102497 | 102504 | 7 | 161 |  | 9.4706
Domestic Zone-3 |  |  | KL | 97662 | 97668 | 6 | 241 |  | 14.1765
Flush Zone -1 |  |  | KL | 149723 | 149725 | 2 | 192 |  | 11.2941
Flush Zone -2 |  |  | KL | 7267 | 7287 | 20 | 102 |  | 6
Flush Zone -3 |  |  | KL | 5247 | 5250 | 3 | 112 |  | 6.5882
Total water consum | [5 empty] | 83 | 1561 |  | 91.8235
Water Branches
Branches
Swimming pool |  |  | KL | 7473 | 7473 | 0 | 57 |  | 3.3529
B2 Laundry |  |  | KL | 35875 | 35889 | 14 | 64 |  | 3.7647
Boiler Feed Water |  |  | KL | 19663 | 19669 | 6 | 130 |  | 7.6471
Total |  |  |  | 0 |  | 20 | 209 |  | 12.2941
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62019 | 62039 | 20 | 101 |  | 5.9412
STP flush(new water meter) |  |  | KL | 32401 | 32401 | 0 | 12 |  | 0.70588
Garden Water Pump |  |  | KL | 4509 | 4509 | 0 | 255 |  | 15
Total |  |  |  | 0 |  | 20 | 735 |  | 43.2353
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11367 | 11389 | 22 | 22 |  | 1.2941
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8206 | 8214 | 8 | 60 |  | 3.5294
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 5.5882
Total | [5 empty] | 30 | 102 |  | 6
Total Domestic Water (R.O +BMC) |  |  | KL |  | 56 | 56 | 68 |  | 4
Total Domestic Consumption |  |  | KL |  | 81 | 81 | 86 |  | 5.0588
Total STP Consumption |  |  | KL |  | 20 | 20 | 26 |  | 1.5294
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 829338 | 829552 | 214 | 3463.54 |  | 203.7376
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145593 | 145639 | 46 | 951.56 |  | 55.9741
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.076471
Boiler Gas Consumption | [5 empty] | 302 | 353 |  | 20.7647
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40031.52 | 40031.52 | 0 | 285.04 |  | 16.7671
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41492.65 | 41517.1 | 24.45 | 132.1 |  | 7.7706
Chiller - 4 |  |  | hr | 32582.98 | 32582.98 | 0 | -0.02 |  | -0.0011765
Steam Boiler -1 |  |  | hr | 22766.92 | 22773.2 | 6.28 | 33.61 | 30.73 | 1.9771
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 0.13 |  | 0.0076471
Steam Boiler -3 |  |  | hr | 70361.47 | 70361.47 | 0 | 45.66 | 0 | 2.6859
Hot Water Generator -1 |  |  | hr | 1739.48 | 1747.53 | 8.05 | 130.67 |  | 7.6865
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0070588
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 3349 | 70663.33 |  | 4156.6665
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 22.52% | 4.5248 |  | 0.26616
Total Chillers Units |  |  | kwh |  |  | 4494 | 82327 |  | 4842.7647
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 30.22% | 5.28 |  | 0.31059
Total Lighting Units |  |  | kwh |  |  | 2646 | 39473 |  | 2321.9412
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 17.79% | 2.5312 |  | 0.14889
Total power Units |  |  | Kwh |  |  | 1050 | 20188 |  | 1187.5294
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.06% | 1.2934 |  | 0.076079
Total mansion power Units |  |  | Kwh |  |  | 762 | 17928 |  | 1054.5882
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.124% | 1.1408 |  | 0.067106
Total fire & em, power Units |  |  | Kwh |  |  | 1338.13 | 20916 |  | 1230.3529
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 8.998% | 1.3421 |  | 0.078948
Lower Basement |  |  | KWh | 37232 | 37311 | 79
upper basement |  |  | KWh | 89007 | 89400 | 393
Level 1 |  |  | KWh | 41864 | 42078 | 214
Level 2 |  |  | KWh | 6402 | 6420 | 18
2nd floor plant room |  |  | KWh | 20419.18 | 20419 | -0.18
5th floor spa |  |  | KWh | 2419 | 2423 | 4
5th Floor |  |  | KWh | 156604 | 156870 | 266
12th Floor |  |  | KWh | 157667 | 157951 | 284
20th Floor |  |  | KWh | 52707 | 52979 | 272
27th Floor |  |  | KWh | 246073 | 246395 | 322
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 80185 | 80272 | 87
1938.82

## 18
Daily Utility Consumption Report
Prepaired by--Nilesh | 2021-05-18 | occupancy | 54% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 29 | Last year same month avg |  | 0% | 0 | 0 | 0
|  | humidity | 79%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 110754 | 126096 | 15342 | 281119 | 12000 | 15617.7222
BEST supply |  |  | KVAH | 111639 | 127135 | 15496 | 282894 | 12000 | 15716.3333
Transformer - 1 - 2500KVA |  |  | kwh | 1247690 | 1262526 | 14836 | 271812 | -3617.7222 | 15100.6667
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0 |  | 14630
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 14836 | 257291 | 506 | 14293.9444
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1677980 | 1678380 | 400 | 7723 | 800 | 429.0556
370.9444
WATER CONSUMPTION
Tankers |  |  | KL | 2 | 0 | 0 | 640 | 65 | 35.5556
BMC |  |  | KL | 138744 | 138849 | 105 | 1037 |  | 57.6111
Total water | [5 empty] | 105 | 1677 | -28.1667 | 93.1667
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2900 | 2900 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4250 | 4250 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 15496 | 9 | 139464 | 2546046 |  | 141447
C.N.G |  |  | Cu.Mtr | 400 | 51.45 | 20580 | 386865.829 |  | 21492.5461
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 105 | 134 | 14070 | 138958 |  | 7719.8889
Water Tanker |  |  | KL | 0 | 80 | 0 | 51200
Total cost | [5 empty] | 174114 | 3123069.829 |  | 173503.8794
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 920574 | 922104 | 1530 | 35645 |  | 1980.2778
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 136.5
Fire Emergency Power Panel - 1000A |  |  | kwh | 116141 | 117395 | 1254 | 22170 |  | 1231.6667
Main Power Panel -1600A |  |  | kwh | 139784 | 140865 | 1081 | 21269 |  | 1181.6111
Main Lighting and Small power Panel |  |  | kwh | 277493 | 279594 | 2101 | 32941 |  | 1830.0556
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 430 | 519 | 89 | 518.77 |  | 28.8206
Chiller No 1 |  |  | kwh | 239668 | 239668 | 0 | 58140 |  | 3230
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 1010795 | 1012910 | 2115 | 38952 |  | 2164
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 187.49 | 187.44 | -0.05 | -0.05 |  | -0.0027778
Sub Total | [5 empty] | 8169.95 | 212093.21 |  | 11782.9561
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0 | 260979.13
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 490007 | 490809 | 802 | 15334 |  | 851.8889
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | -0.07 |  | -0.0038889
Main Lighting and Small power Panel |  |  | kwh | 424944 | 425468 | 524 | 8634 |  | 479.6667
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12622 | 12700 | 78 | 4938 |  | 274.3333
Chiller No -3 - 1200A |  |  | kwh | 24040 | 29124.54 | 5084.54 | 29124.54 |  | 1618.03
Chiller No-4 - 1200A |  |  | Kwh | 589435.47 | 589435.47 | 0 | 147.11 |  | 8.1728
Chiller Water pump Panel- 630A |  |  | kwh | 7711.33 | 7711.33 | 0 | 0.33 |  | 0.018333
B2-Loundry power panel |  |  | kwh | 48104 | 48167 | 63 | 1450 |  | 80.5556
Sub Total | [5 empty] | 6551.54 | 59627.98 | 620.51 | 3312.6656
|  |  | Total TR1 & TR2 |  |  | 14721.49 | 273305.08 | 114.51 | 15183.6156
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419.18 | 0.18 | 0.362 |  | 0.020111
5th floor spa |  |  | KWh | 2423 | 2427 | 4 | 68 |  | 3.7778
5th Floor |  |  | KWh | 156870 | 157207 | 337 | 3908 |  | 217.1111
12th Floor |  |  | KWh | 157951 | 158219 | 268 | 3620 |  | 201.1111
20th Floor |  |  | KWh | 52979 | 53249 | 270 | 4678 |  | 259.8889
27th Floor |  |  | KWh | 246395 | 246695 | 300 | 3521 |  | 195.6111
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 80272 | 80350 | 78 | 1356 |  | 75.3333
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855696 | 855702 | 6 | 230 |  | 12.7778
Main kitchen power panel no 2 |  |  | KWh | 885893 | 885895 | 2 | 199 |  | 11.0556
Prato kitchen power panel |  |  | KWh | 2495 | 2499 | 4 | 220 |  | 12.2222
San- Qi Indian Kitchen |  |  | KWh | 11880 | 11933 | 53 | 963 |  | 53.5
San- Qi Japanese Kitchen |  |  | KWh | 6635 | 6691 | 56 | 974.05 |  | 54.1139
The club kitchen |  |  | KWh | 702294 | 702324 | 30 | 762 |  | 42.3333
AER Kitchen |  |  | KWh | 671474 | 671549 | 75 | 1524 |  | 84.6667
COLD ROOM'S |  |  | KWh | 829167 | 829295 | 128 | 1564 |  | 86.8889
Ball Room 1 kitchen |  |  | KWh | 522731 | 523031 | 300 | 3570 |  | 198.3333
Ball Room 2 kitchen |  |  | KWh | 637752 | 637832 | 80 | 1354 |  | 75.2222
B1 Laundry |  |  | kwh | 107930 | 107956 | 26 | 344 |  | 19.1111
STP Electrical |  |  | kwh | 18079 | 18319 | 240 | 3548 |  | 197.1111
Cooling Tower |  |  | kwh | 491626 | 491979 | 353 | 11846 |  | 658.1111
Total | [5 empty] | 1353 | 30607 |  | 1700.3889
MOCK Up Room |  |  | Kwh | 460478 | 460509 | 31 | 31 |  | 1.7222
27th Floor |  |  | Kwh | 81116 | 81130 | 14 | 14 |  | 0.77778
Physic57 |  |  | Kwh | 152520 | 152588 | 68 | 68 |  | 3.7778
Pinoor Legal- Lighting |  |  | Kwh | 64943 | 64950 | 7 | 7 |  | 0.38889
Pinoor Legal- Lighting |  |  | Kwh | 3272.5 | 3272.7 | 0.2 | 0.2 |  | 0.011111
20th Floor Project office |  |  | kwh | 27957 | 27959 | 2 | 2
WATER
R.o.plant |  |  | KL | 245077 | 245077 | 0 | 553 |  | 30.7222
STP Water Prod |  |  | KL | 184915 | 185061 | 146 | 1530 |  | 85
Total water Produce |  |  |  | 0 |  | 146 | 1936 |  | 107.5556
Domestic Zone-1 |  |  | KL | 413639 | 413668 | 29 | 782 |  | 43.4444
Domestic Zone-2 |  |  | KL | 102504 | 102516 | 12 | 173 |  | 9.6111
Domestic Zone-3 |  |  | KL | 97668 | 97676 | 8 | 249 |  | 13.8333
Flush Zone -1 |  |  | KL | 149725 | 149729 | 4 | 196 |  | 10.8889
Flush Zone -2 |  |  | KL | 7287 | 7293 | 6 | 108 |  | 6
Flush Zone -3 |  |  | KL | 5250 | 5254 | 4 | 116 |  | 6.4444
Total water consum | [5 empty] | 63 | 1624 |  | 90.2222
Water Branches
Branches
Swimming pool |  |  | KL | 7473 | 7473 | 0 | 57 |  | 3.1667
B2 Laundry |  |  | KL | 35889 | 35889 | 0 | 50 |  | 2.7778
Boiler Feed Water |  |  | KL | 19669 | 19671 | 2 | 126 |  | 7
Total |  |  |  | 0 |  | 2 | 191 |  | 10.6111
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62039 | 62112 | 73 | 154 |  | 8.5556
STP flush(new water meter) |  |  | KL | 32401 | 32401 | 0 | 12 |  | 0.66667
Garden Water Pump |  |  | KL | 4509 | 4513 | 4 | 259 |  | 14.3889
Total |  |  |  | 0 |  | 77 | 792 |  | 44
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11389 | 11399 | 10 | 10 |  | 0.55556
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8214 | 8214 | 0 | 52 |  | 2.8889
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 5.2778
Total | [5 empty] | 10 | 82 |  | 4.5556
Total Domestic Water (R.O +BMC) |  |  | KL |  | 105 | 105 | 117 |  | 6.5
Total Domestic Consumption |  |  | KL |  | 59 | 59 | 64 |  | 3.5556
Total STP Consumption |  |  | KL |  | 77 | 77 | 83 |  | 4.6111
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 829552 | 829747 | 195 | 3658.54 |  | 203.2522
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145639 | 145684 | 45 | 996.56 |  | 55.3644
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.072222
Boiler Gas Consumption | [5 empty] | 160 | 513 |  | 28.5
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40031.52 | 40031.52 | 0 | 285.04 |  | 15.8356
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41517.1 | 41541 | 23.9 | 156 |  | 8.6667
Chiller - 4 |  |  | hr | 32582.98 | 32582.98 | 0 | -0.02 |  | -0.0011111
Steam Boiler -1 |  |  | hr | 22773.2 | 22773.2 | 0 | 33.61 | 23.9 | 1.8672
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 0.13 |  | 0.0072222
Steam Boiler -3 |  |  | hr | 70361.47 | 70370 | 8.53 | 54.19 | 8.53 | 3.0106
Hot Water Generator -1 |  |  | hr | 1747.53 | 1755.27 | 7.74 | 138.41 |  | 7.6894
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0066667
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 3645 | 74308.33 |  | 4128.2406
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 23.76% | 4.7624 |  | 0.26458
Total Chillers Units |  |  | kwh |  |  | 5084.54 | 87411.54 |  | 4856.1967
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 33.14% | 5.6114 |  | 0.31174
Total Lighting Units |  |  | kwh |  |  | 2625 | 42098 |  | 2338.7778
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 17.11% | 2.7023 |  | 0.15013
Total power Units |  |  | Kwh |  |  | 1081 | 21269 |  | 1181.6111
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.046% | 1.3638 |  | 0.075767
Total mansion power Units |  |  | Kwh |  |  | 802 | 18730 |  | 1040.5556
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.227% | 1.1931 |  | 0.066282
Total fire & em, power Units |  |  | Kwh |  |  | 1254 | 22170 |  | 1231.6667
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 8.174% | 1.4238 |  | 0.079103
Lower Basement |  |  | KWh | 37311 | 37386 | 75
upper basement |  |  | KWh | 89400 | 89789 | 389
Level 1 |  |  | KWh | 42078 | 42288 | 210
Level 2 |  |  | KWh | 6420 | 6441 | 21
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2423 | 2427 | 4
5th Floor |  |  | KWh | 156870 | 157207 | 337
12th Floor |  |  | KWh | 157951 | 158219 | 268
20th Floor |  |  | KWh | 52979 | 53249 | 270
27th Floor |  |  | KWh | 246395 | 246695 | 300
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 80272 | 80350 | 78
1952

## 19
Daily Utility Consumption Report
Prepaired by------- Devendra | 2021-05-19 | occupancy | 10% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 27 | Last year same month avg
|  | humidity | 84%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 126096 | 140515 | 14419 | 295538 | 12000 | 15554.6316
BEST supply |  |  | KVAH | 127135 | 141684 | 14549 | 297443 | 12000 | 15654.8947
Transformer - 1 - 2500KVA |  |  | kwh | 1262526 | 1276465 | 13939 | 285751 | -3654.8947 | 15039.5263
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 13939 | 271230 | 480 | 14275.2632
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1678380 | 1678628 | 248 | 7971 | 800 | 419.5263
380.4737
WATER CONSUMPTION
Tankers |  |  | KL | 0 | 0 | 0 | 640 | 65 | 33.6842
BMC |  |  | KL | 138849 | 138909 | 60 | 1097 |  | 57.7368
Total water | [5 empty] | 60 | 1737 | -26.4211 | 91.4211
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 14549 | 9 | 130941 | 2676987 |  | 140894.0526
C.N.G |  |  | Cu.Mtr | 248 | 51.45 | 12759.6 | 399625.429 |  | 21032.9173
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 60 | 134 | 8040 | 146998 |  | 7736.7368
Water Tanker |  |  | KL | 0 | 80 | 0 | 51200 |  | 2694.7368
Total cost | [5 empty] | 151740.6 | 3274810.429 |  | 172358.4436
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 922104 | 923755 | 1651 | 37296 |  | 1962.9474
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 129.3158
Fire Emergency Power Panel - 1000A |  |  | kwh | 117395 | 118595 | 1200 | 23370 |  | 1230
Main Power Panel -1600A |  |  | kwh | 140865 | 141864 | 999 | 22268 |  | 1172
Main Lighting and Small power Panel |  |  | kwh | 279594 | 281607 | 2013 | 34954 |  | 1839.6842
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 519 | 587 | 68 | 586.77 |  | 30.8826
Chiller No 1 |  |  | kwh | 239668 | 239668 | 0 | 58140 |  | 3060
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 1012910 | 1014999 | 2089 | 41041 |  | 2160.0526
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 0 | 0 | 0 | -0.05 |  | -0.0026316
Sub Total |  |  |  | 0 | 0 | 8020 | 220113.21 |  | 11584.9058
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732 | -0.13 | -0.13 |  | -0.0068421
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 490809 | 491602 | 793 | 16127 |  | 848.7895
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | -0.07 |  | -0.0036842
Main Lighting and Small power Panel |  |  | kwh | 425444 | 426010 | 566 | 9200 |  | 484.2105
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12700 | 12782 | 82 | 5020 |  | 264.2105
Chiller No -3 - 1200A |  |  | kwh | 29124.54 | 33528 | 4403.46 | 33528 |  | 1764.6316
Chiller No-4 - 1200A |  |  | Kwh | 589435.47 | 589484 | 48.53 | 195.64 |  | 10.2968
Chiller Water pump Panel- 630A |  |  | kwh | 7711.33 | 7711 | -0.33 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 48167 | 48168 | 1 | 1451 |  | 76.3684
Sub Total | [5 empty] | 5893.53 | 65521.51 | 505.47 | 3448.5005
|  |  | Total TR1 & TR2 |  |  | 13913.53 | 287218.61 | 25.47 | 15116.7689
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419.18 | 20419.2 | 0.02 | 0.382 |  | 0.020105
5th floor spa |  |  | KWh | 2427 | 2431 | 4 | 72 |  | 3.7895
5th Floor |  |  | KWh | 157207 | 157530 | 323 | 4231 |  | 222.6842
12th Floor |  |  | KWh | 158219 | 158429 | 210 | 3830 |  | 201.5789
20th Floor |  |  | KWh | 53249 | 53483 | 234 | 4912 |  | 258.5263
27th Floor |  |  | KWh | 246695 | 246931 | 236 | 3757 |  | 197.7368
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 80350 | 80454 | 104 | 1460 |  | 76.8421
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855702 | 855712 | 10 | 240 |  | 12.6316
Main kitchen power panel no 2 |  |  | KWh | 885895 | 885896 | 1 | 200 |  | 10.5263
Prato kitchen power panel |  |  | KWh | 2499 | 2504 | 5 | 225 |  | 11.8421
San- Qi Indian Kitchen |  |  | KWh | 11933 | 11989 | 56 | 1019 |  | 53.6316
San- Qi Japanese Kitchen |  |  | KWh | 6691 | 6749 | 58 | 1032.05 |  | 54.3184
The club kitchen |  |  | KWh | 702324 | 702353 | 29 | 791 |  | 41.6316
AER Kitchen |  |  | KWh | 671549 | 671631 | 82 | 1606 |  | 84.5263
COLD ROOM'S |  |  | KWh | 829295 | 829418 | 123 | 1687 |  | 88.7895
Ball Room 1 kitchen |  |  | KWh | 523031 | 523324 | 293 | 3863 |  | 203.3158
Ball Room 2 kitchen |  |  | KWh | 637832 | 637909 | 77 | 1431 |  | 75.3158
B1 Laundry |  |  | kwh | 107956 | 107967 | 11 | 355 |  | 18.6842
STP Electrical |  |  | kwh | 18319 | 18472 | 153 | 3701 |  | 194.7895
Cooling Tower |  |  | kwh | 491979 | 492334 | 355 | 12201 |  | 642.1579
Total | [5 empty] | 1253 | 31860 |  | 1676.8421
MOCK Up Room |  |  | Kwh | 460509 | 460532 | 23 | 54 |  | 2.8421 | 424609 | -35923
27th Floor |  |  | Kwh | 81130 | 81151 | 21 | 35 |  | 1.8421
Physic57 |  |  | Kwh | 152588 | 152612 | 24 | 92 |  | 4.8421
Pinoor Legal- Lighting |  |  | Kwh | 64950 | 64956 | 6 | 13 |  | 0.68421
Pinoor Legal- Lighting |  |  | Kwh | 3272.7 | 3272.7 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27959 | 27966 | 7
WATER
R.o.plant |  |  | KL | 244977 | 244977 | 0 | 553 |  | 29.1053
STP Water Prod |  |  | KL | 185061 | 185136 | 75 | 1605 |  | 84.4737
Total water Produce |  |  |  | 0 |  | 75 | 2011 |  | 105.8421
Domestic Zone-1 |  |  | KL | 413668 | 413691 | 23 | 805 |  | 42.3684
Domestic Zone-2 |  |  | KL | 102516 | 102523 | 7 | 180 |  | 9.4737
Domestic Zone-3 |  |  | KL | 97676 | 97688 | 12 | 261 |  | 13.7368
Flush Zone -1 |  |  | KL | 149729 | 149740 | 11 | 207 |  | 10.8947
Flush Zone -2 |  |  | KL | 7293 | 7299 | 6 | 114 |  | 6
Flush Zone -3 |  |  | KL | 5254 | 5257 | 3 | 119 |  | 6.2632
Total water consum | [5 empty] | 62 | 1686 |  | 88.7368
Water Branches
Branches
Swimming pool |  |  | KL | 7473 | 7473 | 0 | 57 |  | 3
B2 Laundry |  |  | KL | 35889 | 35889 | 0 | 50 |  | 2.6316
Boiler Feed Water |  |  | KL | 19671 | 19671 | 0 | 126 |  | 6.6316
Total |  |  |  | 0 |  | 0 | 191 |  | 10.0526
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62112 | 62152 | 40 | 194 |  | 10.2105
STP flush(new water meter) |  |  | KL | 32401 | 32412 | 11 | 23 |  | 1.2105
Garden Water Pump |  |  | KL | 4513 | 4513 | 0 | 259 |  | 13.6316
Total |  |  |  | 0 |  | 51 | 843 |  | 44.3684
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11399 | 11406 | 7 | 17 |  | 0.89474
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8214 | 8216 | 2 | 54 |  | 2.8421
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 5
Total | [5 empty] | 9 | 91 |  | 4.7895
Total Domestic Water (R.O +BMC) |  |  | KL |  | 60 | 60 | 177 |  | 9.3158
Total Domestic Consumption |  |  | KL |  | 51 | 51 | 115 |  | 6.0526
Total STP Consumption |  |  | KL |  | 51 | 51 | 134 |  | 7.0526
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 829747 | 829920 | 173 | 3831.54 |  | 201.66
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145684 | 145726 | 42 | 1038.56 |  | 54.6611
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.068421
Boiler Gas Consumption | [5 empty] | 33 | 546 |  | 28.7368
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40031.52 | 40031.52 | 0 | 285.04 |  | 15.0021
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41541 | 41565 | 24 | 180 |  | 9.4737
Chiller - 4 |  |  | hr | 32582.98 | 32582.92 | -0.06 | -0.08 |  | -0.0042105
Steam Boiler -1 |  |  | hr | 22773.2 | 22773.2 | 0 | 33.61 | 23.94 | 1.7689
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 0.13 |  | 0.0068421
Steam Boiler -3 |  |  | hr | 70370 | 70370.02 | 0.02 | 54.21 | 0.02 | 2.8532
Hot Water Generator -1 |  |  | hr | 1755.27 | 1762.57 | 7.3 | 145.71 |  | 7.6689
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0063158
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 3739.54 | 78047.87 |  | 4107.7826
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 25.93% | 5.0217 |  | 0.2643
Total Chillers Units |  |  | kwh |  |  | 4451.99 | 91863.53 |  | 4834.9226
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 30.88% | 5.9202 |  | 0.31159
Total Lighting Units |  |  | kwh |  |  | 2579 | 44677 |  | 2351.4211
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 17.89% | 2.8811 |  | 0.15164
Total power Units |  |  | Kwh |  |  | 999 | 22268 |  | 1172
% of power Units of Total Con.(LT) |  |  | % |  |  | 6.928% | 1.4331 |  | 0.075426
Total mansion power Units |  |  | Kwh |  |  | 793 | 19523 |  | 1027.5263
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.5% | 1.2481 |  | 0.065688
Total fire & em, power Units |  |  | Kwh |  |  | 1200 | 23370 |  | 1230
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 8.322% | 1.5071 |  | 0.079319
Lower Basement |  |  | KWh | 37386 | 37462 | 76
upper basement |  |  | KWh | 89789 | 90173 | 384
Level 1 |  |  | KWh | 42288 | 42495 | 207
Level 2 |  |  | KWh | 6441 | 6460 | 19
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2427 | 2431 | 4
5th Floor |  |  | KWh | 157207 | 106166 | 323
12th Floor |  |  | KWh | 158219 | 116811.03 | 210
20th Floor |  |  | KWh | 53249 | 9380.09 | 234
27th Floor |  |  | KWh | 246695 | 180787.83 | 236
34th Floor |  |  | KWh | 85321 | 59451.31 | 0
Sanqi |  |  | KWh | 80350 | 52064.98 | 104
1797
20th Floor project office meter reading |  |  | KWh |  |  | 0

## 20
Daily Utility Consumption Report
Prepaired by -- Devendra | 2021-05-20 | occupancy | 24% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 27 | Last year same month avg |  | 0 | 0 | 0 | 0
|  | humidity | 84%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 140515 | 155638 | 15123 | 310661 | 12000 | 15533.05 | 11998 | 3125
BEST supply |  |  | KVAH | 141684 | 156915 | 15231 | 312674 | 12000 | 15633.7
Transformer - 1 - 2500KVA |  |  | kwh | 1276465 | 1291086 | 14621 | 300372 | -3633.7 | 15018.6
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 14621 | 285851 | 502 | 14292.55
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1678628 | 1678916 | 288 | 8259 | 800 | 412.95
387.05
WATER CONSUMPTION
Tankers |  |  | KL | 0 | 0 | 0 | 640 | 65 | 32
BMC |  |  | KL | 138909 | 138966 | 57 | 1154 |  | 57.7
Total water | [5 empty] | 57 | 1794 | -24.7 | 89.7
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 15231 | 9 | 137079 | 2814066 |  | 140703.3
C.N.G |  |  | Cu.Mtr | 288 | 51.45 | 14817.6 | 414443.029 |  | 20722.1514
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 57 | 134 | 7638 | 154636 |  | 7731.8
Water Tanker |  |  | KL | 0 | 80 | 0 | 51200 |  | 2560
Total cost | [5 empty] | 159534.6 | 3434345.029 |  | 171717.2515
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 923755 | 925573 | 1818 | 39114 |  | 1955.7 | 1457.28 | 360.72
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 122.85 | 483.93 | -483.93
Fire Emergency Power Panel - 1000A |  |  | kwh | 118595 | 119850 | 1255 | 24625 |  | 1231.25 | 1173.92 | 81.08
Main Power Panel -1600A |  |  | kwh | 141864 | 142842 | 978 | 23246 |  | 1162.3 | 0 | 978
Main Lighting and Small power Panel |  |  | kwh | 281607 | 283568 | 1961 | 36915 |  | 1845.75 | 1987.04 | -26.04
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 587 | 587 | 0 | 586.77 |  | 29.3385 | 0 | 0
Chiller No 1 |  |  | kwh | 239668 | 239668 | 0 | 58140 |  | 2907 | 0 | 0
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0 | 3246.45 | -3246.45
Chiller Water pump Panel- 630A |  |  | kwh | 1014999 | 1017117 | 2118 | 43159 |  | 2157.95 | 1559.2 | 558.8
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Lawn Pantry |  |  | kwh | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Pavilion Power |  |  | kwh | 0 | 0 | 0 | -0.05 |  | -0.0025 | 0 | 0
Sub Total | [5 empty] | 8130 | 228243.21 |  | 11412.1605 | 9907.82 | -1777.82
Transformer No 2 (Sub Feeders) | [10 empty] | 0
Main HVAC Power Panel- 800A |  |  | kwh | 260732 | 260732 | 0 | -0.13 |  | -0.0065 | 0 | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 491602 | 492472 | 870 | 16997 |  | 849.85 | 631.67 | 238.33
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0 | 0 | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | -0.07 |  | -0.0035 | 1057.52 | -1057.52
Main Lighting and Small power Panel |  |  | kwh | 426010 | 426566 | 556 | 9756 |  | 487.8 | 106.49 | 449.51
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12782 | 12865 | 83 | 5103 |  | 255.15 | 0 | 83
Chiller No -3 - 1200A |  |  | kwh | 33528 | 38262 | 4734 | 38262 |  | 1913.1 | 0 | 4734
Chiller No-4 - 1200A |  |  | Kwh | 589484 | 589494 | 10 | 205.64 |  | 10.282 | 0 | 10
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0 | 0 | 0
B2-Loundry power panel |  |  | kwh | 48168 | 48183 | 15 | 1466 |  | 73.3 | 0 | 15
Sub Total | [5 empty] | 6268 | 71789.51 | 725 | 3589.4755 | 1795.68 | 4472.32
|  |  | Total TR1 & TR2 |  |  | 14398 | 301616.61 | 223 | 15080.8305 | 11703.5 | 2694.5
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419.2 | 20419.2 | 0 | 0.382 |  | 0.0191
5th floor spa |  |  | KWh | 2431 | 2435 | 4 | 76 |  | 3.8
5th Floor |  |  | KWh | 157530 | 157797 | 267 | 4498 |  | 224.9
12th Floor |  |  | KWh | 158429 | 158634 | 205 | 4035 |  | 201.75
20th Floor |  |  | KWh | 53483 | 53739 | 256 | 5168 |  | 258.4
27th Floor |  |  | KWh | 246931 | 247210 | 279 | 4036 |  | 201.8
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 80454 | 80521 | 67 | 1527 |  | 76.35
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855712 | 855721 | 9 | 249 |  | 12.45
Main kitchen power panel no 2 |  |  | KWh | 885896 | 885896 | 0 | 200 |  | 10
Prato kitchen power panel |  |  | KWh | 2504 | 2512 | 8 | 233 |  | 11.65
San- Qi Indian Kitchen |  |  | KWh | 11989 | 12041 | 52 | 1071 |  | 53.55
San- Qi Japanese Kitchen |  |  | KWh | 6749 | 6806 | 57 | 1089.05 |  | 54.4525
The club kitchen |  |  | KWh | 702353 | 702386 | 33 | 824 |  | 41.2
AER Kitchen |  |  | KWh | 671631 | 671681 | 50 | 1656 |  | 82.8
COLD ROOM'S |  |  | KWh | 829418 | 829535 | 117 | 1804 |  | 90.2
Ball Room 1 kitchen |  |  | KWh | 523324 | 523681 | 357 | 4220 |  | 211
Ball Room 2 kitchen |  |  | KWh | 637909 | 637985 | 76 | 1507 |  | 75.35
B1 Laundry |  |  | kwh | 107967 | 107977 | 10 | 365 |  | 18.25
STP Electrical |  |  | kwh | 18472 | 18566 | 94 | 3795 |  | 189.75
Cooling Tower |  |  | kwh | 492334 | 492699 | 365 | 12566 |  | 628.3
Total | [5 empty] | 1228 | 33088 |  | 1654.4
MOCK Up Room |  |  | Kwh | 460532 | 460556 | 24 | 78 |  | 3.9
27th Floor |  |  | Kwh | 81151 | 81178 | 27 | 62 |  | 3.1
Physic57 |  |  | Kwh | 152612 | 152635 | 23 | 115 |  | 5.75
Pinoor Legal- Lighting |  |  | Kwh | 64956 | 64961 | 5 | 18 |  | 0.9
Pinoor Legal- Lighting |  |  | Kwh | 3272.7 | 3272.7 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27966 | 27972 | 6 | 6 |  | 0.3
WATER
R.o.plant |  |  | KL | 244977 | 244999 | 22 | 575 |  | 28.75
STP Water Prod |  |  | KL | 185136 | 185170 | 34 | 1639 |  | 81.95
Total water Produce |  |  |  | 0 |  | 56 | 2067 |  | 103.35
Domestic Zone-1 |  |  | KL | 413691 | 413718 | 27 | 832 |  | 41.6
Domestic Zone-2 |  |  | KL | 102523 | 102534 | 11 | 191 |  | 9.55
Domestic Zone-3 |  |  | KL | 97688 | 97704 | 16 | 277 |  | 13.85
Flush Zone -1 |  |  | KL | 149740 | 149750 | 10 | 217 |  | 10.85
Flush Zone -2 |  |  | KL | 7299 | 7308 | 9 | 123 |  | 6.15
Flush Zone -3 |  |  | KL | 5257 | 5262 | 5 | 124 |  | 6.2
Total water consum | [5 empty] | 78 | 1764 |  | 88.2
Water Branches
Branches
Swimming pool |  |  | KL | 7473 | 7473 | 0 | 57 |  | 2.85
B2 Laundry |  |  | KL | 35889 | 35889 | 0 | 50 |  | 2.5
Boiler Feed Water |  |  | KL | 19671 | 19671 | 0 | 126 |  | 6.3
Total |  |  |  | 0 |  | 0 | 191 |  | 9.55
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62152 | 62191 | 39 | 233 |  | 11.65
STP flush(new water meter) |  |  | KL | 32412 | 32430 | 18 | 41 |  | 2.05
Garden Water Pump |  |  | KL | 4513 | 4513 | 0 | 259 |  | 12.95
Total |  |  |  | 0 |  | 57 | 900 |  | 45
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11406 | 11420 | 14 | 31 |  | 1.55
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8216 | 8219 | 3 | 57 |  | 2.85
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 4.75
Total | [5 empty] | 17 | 108 |  | 5.4
Total Domestic Water (R.O +BMC) |  |  | KL |  | 79 | 79 | 256 |  | 12.8
Total Domestic Consumption |  |  | KL |  | 68 | 68 | 183 |  | 9.15
Total STP Consumption |  |  | KL |  | 57 | 57 | 191 |  | 9.55
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 829920 | 830124 | 204 | 4035.54 |  | 201.777
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145726 | 145774 | 48 | 1086.56 |  | 54.328
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.065
Boiler Gas Consumption | [5 empty] | 36 | 582 |  | 29.1
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40031.52 | 40031.52 | 0 | 285.04 |  | 14.252 |  |  |  | -24
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41565 | 41589 | 24 | 204 |  | 10.2
Chiller - 4 |  |  | hr | 32582.92 | 32582.92 | 0 | -0.08 |  | -0.004
Steam Boiler -1 |  |  | hr | 22773.2 | 22773.2 | 0 | 33.61 | 24 | 1.6805
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 0.13 |  | 0.0065
Steam Boiler -3 |  |  | hr | 70370.02 | 70370.02 | 0 | 54.21 | 0 | 2.7105
Hot Water Generator -1 |  |  | hr | 1762.57 | 1770.76 | 8.19 | 153.9 |  | 7.695
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.006
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 3936 | 81983.87 |  | 4099.1935
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 0.26027 | 5.282 |  | 0.2641
Total Chillers Units |  |  | kwh |  |  | 4744 | 96607.53 |  | 4830.3765
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 0.31369 | 6.2338 |  | 0.31169
Total Lighting Units |  |  | kwh |  |  | 2517 | 47194 |  | 2359.7
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 0.16644 | 3.0476 |  | 0.15238
Total power Units |  |  | Kwh |  |  | 978 | 23246 |  | 1162.3
% of power Units of Total Con.(LT) |  |  | % |  |  | 0.06467 | 1.4978 |  | 0.074888
Total mansion power Units |  |  | Kwh |  |  | 870 | 20393 |  | 1019.65
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 0.057528 | 1.3056 |  | 0.06528
Total fire & em, power Units |  |  | Kwh |  |  | 1255 | 24625 |  | 1231.25 |  | Lighting | 0.5 | 50
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 0.082986 | 1.5901 |  | 0.079503
Lower Basement |  |  | KWh | 37462 | 37539 | 77 |  |  |  | 70.4 | 6.6
upper basement |  |  | KWh | 90173 | 90557 | 384 |  |  |  | 124.26 | 259.74
Level 1 |  |  | KWh | 42495 | 42697 | 202 |  |  |  | 138.98 | 63.02
Level 2 |  |  | KWh | 6460 | 6474 | 14 |  |  |  | 45.83 | -31.83
2nd floor plant room |  |  | KWh | 20419.2 | 20419.2 | 0 |  |  |  | -0.18 | 0.18
5th floor spa |  |  | KWh | 2431 | 2435 | 4 |  |  |  | 0 | 4
5th Floor |  |  | KWh | 157530 | 157797 | 267 |  |  |  | 193.55 | 73.45
12th Floor |  |  | KWh | 158429 | 158634 | 205 |  |  |  | 168.4 | 36.6
20th Floor |  |  | KWh | 53483 | 53739 | 256 |  |  |  | 221.19 | 34.81
27th Floor |  |  | KWh | 246931 | 247210 | 279 |  |  |  | 337.19 | -58.19
34th Floor |  |  | KWh | 85321 | 85321 | 0 |  |  |  | 115.09 | -115.09
Sanqi |  |  | KWh | 80454 | 80521 | 67 |  |  |  | 11.8 | 55.2
[6 empty] | 1755 |  |  |  |  | 328.49
20th Floor project office meter reading |  |  | KWh |  |  | 0
.
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## 21
Prepaired by- Devendra | 2021-05-21 | occupancy | 24% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 28 | Last year same month avg |  | 0 | 0 | 0 | 0
|  | humidity | 84%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 155638 | 171650 | 16012 | 326673 | 12000 | 15555.8571 | 12199 | 3813
BEST supply |  |  | KVAH | 156915 | 173011 | 16096 | 328770 | 12000 | 15655.7143 | 12262 | 3834
Transformer - 1 - 2500KVA |  |  | kwh | 1291086 | 1306521 | 15435 | 315807 | -3655.7143 | 15038.4286
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 15435 | 301286 | 577 | 14346.9524
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1678916 | 1679450 | 534 | 8793 | 800 | 418.7143
381.2857
WATER CONSUMPTION
Tankers |  |  | KL | 0 | 4 | 40 | 680 | 65 | 32.381
BMC |  |  | KL | 138966 | 139022 | 56 | 1210 |  | 57.619
Total water | [5 empty] | 96 | 1890 | -25 | 90
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 16096 | 9 | 144864 | 2958930 |  | 140901.4286
C.N.G |  |  | Cu.Mtr | 534 | 51.45 | 27474.3 | 441917.329 |  | 21043.6823
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 56 | 134 | 7504 | 162140 |  | 7720.9524
Water Tanker |  |  | KL | 40 | 80 | 3200 | 54400 |  | 2590.4762
Total cost | [5 empty] | 183042.3 | 3617387.329 |  | 172256.5395
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 925573 | 927416 | 1843 | 40957 |  | 1950.3333 | 1520.28 | 322.72
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 117 | 485.22 | -485.22
Fire Emergency Power Panel - 1000A |  |  | kwh | 119850 | 121183 | 1333 | 25958 |  | 1236.0952 | 1194.9 | 138.1
Main Power Panel -1600A |  |  | kwh | 142842 | 143992 | 1150 | 24396 |  | 1161.7143 | 0 | 1150
Main Lighting and Small power Panel |  |  | kwh | 283568 | 285105 | 1537 | 38452 |  | 1831.0476 | 2147.36 | -610.36
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 587 | 587 | 0 | 586.77 |  | 27.9414 | 0 | 0
Chiller No 1 |  |  | kwh | 239668 | 239668 | 0 | 58140 |  | 2768.5714 | 0 | 0
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0 | 3228.57 | -3228.57
Chiller Water pump Panel- 630A |  |  | kwh | 1017117 | 1019250 | 2133 | 45292 |  | 2156.7619 | 1595.68 | 537.32
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Lawn Pantry |  |  | kwh | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
Pavilion Power |  |  | kwh | 0 | 0 | 0 | -0.05 |  | -0.002381 | 0.05 | -0.05
Sub Total | [5 empty] | 7996 | 236239.21 |  | 11249.4862 | 10172.06 | -2176.06
Transformer No 2 (Sub Feeders) | [10 empty] | 0
Main HVAC Power Panel- 800A |  |  | kwh | 260732 | 260732.13 | 0.13 | 0 |  | 0 | 0 | 0.13
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 492472 | 493272 | 800 | 17797 |  | 847.4762 | 700.87 | 99.13
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0 | 0 | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606.07 | 0.07 | 0 |  | 0 | 985.98 | -985.91
Main Lighting and Small power Panel |  |  | kwh | 426566 | 427132 | 566 | 10322 |  | 491.5238 | 107.6 | 458.4
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12865 | 12947 | 82 | 5185 |  | 246.9048 | 0 | 82
Chiller No -3 - 1200A |  |  | kwh | 38262 | 43396 | 5134 | 43396 |  | 2066.4762 | 0 | 5134
Chiller No-4 - 1200A |  |  | Kwh | 589494 | 589504 | 10 | 215.64 |  | 10.2686 | 0 | 10
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0 | 0 | 0
B2-Loundry power panel |  |  | kwh | 48183 | 48316 | 133 | 1599 |  | 76.1429 | 0 | 133
Sub Total | [5 empty] | 6725.2 | 78514.71 | 1290.8 | 3738.7957 | 1794.45 | 4930.75
|  |  | Total TR1 & TR2 |  |  | 14721.2 | 316337.81 | 713.8 | 15063.7052 | 11966.51 | 2754.69
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419.2 | 20419.2 | 0 | 0.382 |  | 0.01819
5th floor spa |  |  | KWh | 2435 | 2438 | 3 | 79 |  | 3.7619
5th Floor |  |  | KWh | 157797 | 157972 | 175 | 4673 |  | 222.5238
12th Floor |  |  | KWh | 158634 | 158840 | 206 | 4241 |  | 201.9524
20th Floor |  |  | KWh | 53739 | 54000 | 261 | 5429 |  | 258.5238
27th Floor |  |  | KWh | 247210 | 247691 | 481 | 4517 |  | 215.0952
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 80521 | 80597 | 76 | 1603 |  | 76.3333
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855721 | 855731 | 10 | 259 |  | 12.3333
Main kitchen power panel no 2 |  |  | KWh | 885896 | 885898 | 2 | 202 |  | 9.619
Prato kitchen power panel |  |  | KWh | 2512 | 2518 | 6 | 239 |  | 11.381
San- Qi Indian Kitchen |  |  | KWh | 12041 | 12094 | 53 | 1124 |  | 53.5238
San- Qi Japanese Kitchen |  |  | KWh | 6806 | 6861 | 55 | 1144.05 |  | 54.4786
The club kitchen |  |  | KWh | 702386 | 702420 | 34 | 858 |  | 40.8571
AER Kitchen |  |  | KWh | 671681 | 671865 | 184 | 1840 |  | 87.619
COLD ROOM'S |  |  | KWh | 829535 | 829671 | 136 | 1940 |  | 92.381
Ball Room 1 kitchen |  |  | KWh | 523681 | 524012 | 331 | 4551 |  | 216.7143
Ball Room 2 kitchen |  |  | KWh | 637985 | 638064 | 79 | 1586 |  | 75.5238
B1 Laundry |  |  | kwh | 107977 | 108003 | 26 | 391 |  | 18.619
STP Electrical |  |  | kwh | 18566 | 18711 | 145 | 3940 |  | 187.619
Cooling Tower |  |  | kwh | 492699 | 493078 | 379 | 12945 |  | 616.4286
Total | [5 empty] | 1440 | 34528 |  | 1644.1905
MOCK Up Room |  |  | Kwh | 460556 | 460577 | 21 | 99 |  | 4.7143
27th Floor |  |  | Kwh | 81178 | 81200 | 22 | 84 |  | 4
Physic57 |  |  | Kwh | 152635 | 152660 | 25 | 140 |  | 6.6667
Pinoor Legal- Lighting |  |  | Kwh | 64961 | 64972 | 11 | 29 |  | 1.381
Pinoor Legal- Lighting |  |  | Kwh | 3272.7 | 3272.7 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27972 | 27978 | 6 | 12 |  | 0.57143
WATER
R.o.plant |  |  | KL | 244999 | 245036 | 37 | 612 |  | 29.1429
STP Water Prod |  |  | KL | 185170 | 185253 | 83 | 1722 |  | 82
Total water Produce |  |  |  | 0 | 0 | 120 | 2187 |  | 104.1429
Domestic Zone-1 |  |  | KL | 413718 | 413767 | 49 | 881 |  | 41.9524
Domestic Zone-2 |  |  | KL | 102534 | 102543 | 9 | 200 |  | 9.5238
Domestic Zone-3 |  |  | KL | 97704 | 97724 | 20 | 297 |  | 14.1429
Flush Zone -1 |  |  | KL | 149750 | 149756 | 6 | 223 |  | 10.619
Flush Zone -2 |  |  | KL | 7308 | 7313 | 5 | 128 |  | 6.0952
Flush Zone -3 |  |  | KL | 5262 | 5276 | 14 | 138 |  | 6.5714
Total water consum | [5 empty] | 103 | 1867 |  | 88.9048
Water Branches
Branches
Swimming pool |  |  | KL | 7473 | 7480 | 7 | 64 |  | 3.0476
B2 Laundry |  |  | KL | 35889 | 35893 | 4 | 54 |  | 2.5714
Boiler Feed Water |  |  | KL | 19671 | 19676 | 5 | 131 |  | 6.2381
Total |  |  |  | 0 |  | 16 | 207 |  | 9.8571
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62191 | 62230 | 39 | 272 |  | 12.9524
STP flush(new water meter) |  |  | KL | 32430 | 32433 | 3 | 44 |  | 2.0952
Garden Water Pump |  |  | KL | 4513 | 4513 | 0 | 259 |  | 12.3333
Total |  |  |  | 0 |  | 42 | 942 |  | 44.8571
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11420 | 11424 | 4 | 35 |  | 1.6667
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8219 | 8226 | 7 | 64 |  | 3.0476
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 4.5238
Total | [5 empty] | 11 | 119 |  | 5.6667
Total Domestic Water (R.O +BMC) |  |  | KL |  | 93 | 93 | 349 |  | 16.619
Total Domestic Consumption |  |  | KL |  | 97 | 97 | 280 |  | 13.3333
Total STP Consumption |  |  | KL |  | 42 | 42 | 233 |  | 11.0952
0
GAS Branch CONSUMPTION | [6 empty] | 0
H.W.G. Gas meter reading |  |  | m3 | 830124 | 830318 | 194 | 4229.54 |  | 201.4067
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145774 | 145841 | 67 | 1153.56 |  | 54.9314
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.061905
Boiler Gas Consumption | [5 empty] | 273 | 855 |  | 40.7143
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40031.52 | 40031.52 | 0 | 285.04 |  | 13.5733
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41589 | 41613 | 24 | 228 |  | 10.8571
Chiller - 4 |  |  | hr | 32582.92 | 32582.92 | 0 | -0.08 |  | -0.0038095
Steam Boiler -1 |  |  | hr | 22773.2 | 22775.91 | 2.71 | 36.32 | 26.71 | 1.7295
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 0.13 |  | 0.0061905
Steam Boiler -3 |  |  | hr | 70370.02 | 70376.65 | 6.63 | 60.84 | 6.63 | 2.8971
Hot Water Generator -1 |  |  | hr | 1770.76 | 1777.78 | 7.02 | 160.92 |  | 7.6629
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0057143
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 3976.13 | 85960 |  | 4093.3333
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 0.24832 | 5.5303 |  | 0.26335
Total Chillers Units |  |  | kwh |  |  | 5144 | 101751.53 |  | 4845.311
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 0.32126 | 6.5551 |  | 0.31215
Total Lighting Units |  |  | kwh |  |  | 2103 | 49297 |  | 2347.4762
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 0.13134 | 3.1789 |  | 0.15138
Total power Units |  |  | Kwh |  |  | 1150.07 | 24396.07 |  | 1161.7176
% of power Units of Total Con.(LT) |  |  | % |  |  | 0.071826 | 1.5696 |  | 0.074742
Total mansion power Units |  |  | Kwh |  |  | 800 | 21193 |  | 1009.1905
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 0.049963 | 1.3556 |  | 0.064551
Total fire & em, power Units |  |  | Kwh |  |  | 1333 | 25958 |  | 1236.0952
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 0.08325 | 1.6733 |  | 0.079681
Lower Basement |  |  | KWh | 37539 | 37620 | 81 |  |  |  | 68.83 | 12.17
upper basement |  |  | KWh | 90557 | 90943 | 386 |  |  |  | 122.46 | 263.54
Level 1 |  |  | KWh | 42697 | 42901 | 204 |  |  |  | 139.42 | 64.58
Level 2 |  |  | KWh | 6474 | 6483 | 9 |  |  |  | 49.66 | -40.66
2nd floor plant room |  |  | KWh | 20419.2 | 20419.2 | 0 |  |  |  | 0 | 0
5th floor spa |  |  | KWh | 2435 | 2438 | 3 |  |  |  | 0 | 3
5th Floor |  |  | KWh | 157797 | 157972 | 175 |  |  |  | 201.76 | -26.76
12th Floor |  |  | KWh | 158634 | 158840 | 206 |  |  |  | 191.63 | 14.37
20th Floor |  |  | KWh | 53739 | 54000 | 261 |  |  |  | 231.68 | 29.32
27th Floor |  |  | KWh | 247210 | 247691 | 481 |  |  |  | 344.3 | 136.7
34th Floor |  |  | KWh | 85321 | 85321 | 0 |  |  |  | 140.91 | -140.91
Sanqi |  |  | KWh | 80521 | 80597 | 76 |  |  |  | 57.71 | 18.29
1882
20th Floor project office meter reading |  |  | KWh
\

## 22
Daily Utility Consumption Report
Prepaired by---- Devendra | 2021-05-22 | occupancy | 35% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 27 | Last year same month avg |  | 0 | 0 | 0 | 0
|  | humidity | 84%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 171650 | 189409 | 17759 | 344432 | 12000 | 15656
BEST supply |  |  | KVAH | 173011 | 190825 | 17814 | 346584 | 12000 | 15753.8182
Transformer - 1 - 2500KVA |  |  | kwh | 1306521 | 1323735 | 17214 | 333021 | -3753.8182 | 15137.3182
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 17214 | 318500 | 545 | 14477.2727
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1679450 | 1680082 | 632 | 9425 | 800 | 428.4091
371.5909
WATER CONSUMPTION
Tankers |  |  | KL | 4 | 9 | 90 | 770 | 65 | 35
BMC |  |  | KL | 139022 | 139082 | 60 | 1270 |  | 57.7273
Total water | [5 empty] | 150 | 2040 | -27.7273 | 92.7273
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 17814 | 9 | 160326 | 3119256 |  | 141784.3636
C.N.G |  |  | Cu.Mtr | 632 | 51.45 | 32516.4 | 474433.729 |  | 21565.1695
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 60 | 134 | 8040 | 170180 |  | 7735.4545
Water Tanker |  |  | KL | 90 | 80 | 7200 | 61600 |  | 2800
Total cost | [5 empty] | 208082.4 | 3825469.729 |  | 173884.9877
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 927416 | 929336 | 1920 | 42877 |  | 1948.9545
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 111.6818
Fire Emergency Power Panel - 1000A |  |  | kwh | 121183 | 122555 | 1372 | 27330 |  | 1242.2727
Main Power Panel -1600A |  |  | kwh | 143992 | 145272 | 1280 | 25676 |  | 1167.0909
Main Lighting and Small power Panel |  |  | kwh | 285105 | 288057 | 2952 | 41404 |  | 1882
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 587 | 686 | 99 | 685.77 |  | 31.1714
Chiller No 1 |  |  | kwh | 239668 | 240478 | 810 | 58950 |  | 2679.5455
Chiller No 2- |  |  | kwh | 59200 | 59200 | 0 | 0 |  | 0
Chiller Water pump Panel- 630A |  |  | kwh | 1019250 | 1021460 | 2210 | 47502 |  | 2159.1818
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Pavilion Power |  |  | kwh | 0 | 0 | 0 | -0.05 |  | -0.0022727
Sub Total | [5 empty] | 10643 | 246882.21 |  | 11221.9186
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 493272 | 494190 | 918 | 18715 |  | 850.6818
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 427132 | 427676 | 544 | 10866 |  | 493.9091
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 12947 | 13027 | 80 | 5265 |  | 239.3182
Chiller No -3 - 1200A |  |  | kwh | 43396 | 48606 | 5210 | 48606 |  | 2209.3636
Chiller No-4 - 1200A |  |  | Kwh | 589504 | 589514 | 10 | 225.64 |  | 10.2564
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 48316 | 48560 | 244 | 1843 |  | 83.7727
Sub Total | [5 empty] | 7006 | 85520.71 | 110 | 3887.305
|  |  | Total TR1 & TR2 |  |  | 17649 | 333986.81 | -435 | 11221.9186
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419.2 | 20419.2 | 0 | 0.382 |  | 0.017364
5th floor spa |  |  | KWh | 2438 | 2442 | 4 | 83 |  | 3.7727
5th Floor |  |  | KWh | 157972 | 158181 | 209 | 4882 |  | 221.9091
12th Floor |  |  | KWh | 158840 | 159043 | 203 | 4444 |  | 202
20th Floor |  |  | KWh | 54000 | 54311 | 311 | 5740 |  | 260.9091
27th Floor |  |  | KWh | 247691 | 248213 | 522 | 5039 |  | 229.0455
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 80597 | 80703 | 106 | 1709 |  | 77.6818
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855731 | 855741 | 10 | 269 |  | 12.2273
Main kitchen power panel no 2 |  |  | KWh | 885898 | 885899 | 1 | 203 |  | 9.2273
Prato kitchen power panel |  |  | KWh | 2518 | 2526 | 8 | 247 |  | 11.2273
San- Qi Indian Kitchen |  |  | KWh | 12094 | 12148 | 54 | 1178 |  | 53.5455
San- Qi Japanese Kitchen |  |  | KWh | 6861 | 6917 | 56 | 1200.05 |  | 54.5477
The club kitchen |  |  | KWh | 702420 | 702462 | 42 | 900 |  | 40.9091
AER Kitchen |  |  | KWh | 671865 | 672062 | 197 | 2037 |  | 92.5909
COLD ROOM'S |  |  | KWh | 829671 | 829800 | 129 | 2069 |  | 94.0455
Ball Room 1 kitchen |  |  | KWh | 524012 | 524389 | 377 | 4928 |  | 224
Ball Room 2 kitchen |  |  | KWh | 638064 | 638140 | 76 | 1662 |  | 75.5455
B1 Laundry |  |  | kwh | 108003 | 108014 | 11 | 402 |  | 18.2727
STP Electrical |  |  | kwh | 18711 | 18885 | 174 | 4114 |  | 187
Cooling Tower |  |  | kwh | 493078 | 493529 | 451 | 13396 |  | 608.9091
Total | [5 empty] | 1586 | 36114 |  | 1641.5455
MOCK Up Room |  |  | Kwh | 460577 | 460665 | 88 | 187 |  | 8.5
27th Floor |  |  | Kwh | 81200 | 81213 | 13 | 97 |  | 4.4091
Physic57 |  |  | Kwh | 152660 | 152683 | 23 | 163 |  | 7.4091
Pinoor Legal- Lighting |  |  | Kwh | 64972 | 64996 | 24 | 53 |  | 2.4091
Pinoor Legal- Lighting |  |  | Kwh | 3272.7 | 3273.5 | 0.8 | 0.8 |  | 0.036364
20th Floor Project office |  |  |  | 27978 | 27980 | 2 | 14 |  | 0.63636
WATER |  |  |  |  | 3272
R.o.plant |  |  | KL | 245036 | 245099 | 63 | 675 |  | 30.6818
STP Water Prod |  |  | KL | 185253 | 185354 | 101 | 1823 |  | 82.8636
Total water Produce |  |  |  | 0 |  | 164 | 2351 |  | 106.8636
Domestic Zone-1 |  |  | KL | 413767 | 413847 | 80 | 961 |  | 43.6818
Domestic Zone-2 |  |  | KL | 102543 | 102552 | 9 | 209 |  | 9.5
Domestic Zone-3 |  |  | KL | 97724 | 97749 | 25 | 322 |  | 14.6364
Flush Zone -1 |  |  | KL | 149756 | 149769 | 13 | 236 |  | 10.7273
Flush Zone -2 |  |  | KL | 7313 | 7320 | 7 | 135 |  | 6.1364
Flush Zone -3 |  |  | KL | 5276 | 5301 | 25 | 163 |  | 7.4091
Total water consum | [5 empty] | 159 | 2026 |  | 92.0909
Water Branches
Branches
Swimming pool |  |  | KL | 7480 | 7484 | 4 | 61 |  | 2.7727
B2 Laundry |  |  | KL | 35893 | 35906 | 13 | 63 |  | 2.8636
Boiler Feed Water |  |  | KL | 19676 | 19680 | 4 | 128 |  | 5.8182
Total |  |  |  | 0 |  | 21 | 210 |  | 9.5455
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62230 | 62270 | 40 | 121 |  | 5.5
STP flush(new water meter) |  |  | KL | 32433 | 32459 | 26 | 38 |  | 1.7273
Garden Water Pump |  |  | KL | 4513 | 4527 | 14 | 269 |  | 12.2273
Total |  |  |  | 0 |  | 80 | 795 |  | 36.1364
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11424 | 11434 | 10 | 10 |  | 0.45455
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8226 | 8243 | 17 | 69 |  | 3.1364
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 4.3182
Total | [5 empty] | 27 | 99 |  | 4.5
Total Domestic Water (R.O +BMC) |  |  | KL |  | 123 | 123 | 135 |  | 6.1364
Total Domestic Consumption |  |  | KL |  | 146 | 146 | 151 |  | 6.8636
Total STP Consumption |  |  | KL |  | 80 | 80 | 86 |  | 3.9091
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 830318 | 830512 | 194 | 4423.54 |  | 201.07
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145841 | 145905 | 64 | 1217.56 |  | 55.3436
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.059091
Boiler Gas Consumption | [5 empty] | 374 | 1229 |  | 55.8636
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40031.52 | 40035.1 | 3.58 | 288.62 |  | 13.1191
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 3.58 | 0
Chiller - 3 |  |  | hr | 41613 | 41637 | 24 | 252 |  | 11.4545
Chiller - 4 |  |  | hr | 32582.92 | 32582.93 | 0.01 | -0.07 |  | -0.0031818
Steam Boiler -1 |  |  | hr | 22775.91 | 22783.45 | 7.54 | 43.86 | 31.55 | 1.9936
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 0.13 |  | 0.0059091
Steam Boiler -3 |  |  | hr | 70376.65 | 70376.65 | 0 | 60.84 | 0 | 2.7655
Hot Water Generator -1 |  |  | hr | 1777.78 | 1785.14 | 7.36 | 168.28 |  | 7.6491
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0054545
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4130 | 90090 |  | 4095
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 0.23256 | 5.7629 |  | 0.26195
Total Chillers Units |  |  | kwh |  |  | 6030 | 107781.53 |  | 4899.1605
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 0.33955 | 6.8947 |  | 0.31339
Total Lighting Units |  |  | kwh |  |  | 3496 | 52793 |  | 2399.6818
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 0.19686 | 3.3758 |  | 0.15344
Total power Units |  |  | Kwh |  |  | 1280 | 25676.07 |  | 1167.0941
% of power Units of Total Con.(LT) |  |  | % |  |  | 0.072076 | 1.6417 |  | 0.074621
Total mansion power Units |  |  | Kwh |  |  | 918 | 22111 |  | 1005.0455
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 0.051692 | 1.4073 |  | 0.063966
Total fire & em, power Units |  |  | Kwh |  |  | 1372 | 27330 |  | 1242.2727
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 0.077257 | 1.7506 |  | 0.079571
Lower Basement |  |  | KWh | 37620 | 37700 | 80 | 68.81
upper basement |  |  | KWh | 90943 | 91314 | 371 | 128.57
Level 1 |  |  | KWh | 42901 | 43101 | 200 | 141.49
Level 2 |  |  | KWh | 6483 | 6493 | 10 | 45.43
2nd floor plant room |  |  | KWh | 20419.2 | 20419 | 0 | 0
5th floor spa |  |  | KWh | 2438 | 2442 | 4 | 0
5th Floor |  |  | KWh | 157972 | 158181 | 209 | 178.52
12th Floor |  |  | KWh | 158840 | 159043 | 203 | 198.39
20th Floor |  |  | KWh | 54000 | 54311 | 311 | 226.35
27th Floor |  |  | KWh | 247691 | 248213 | 522 | 312.47
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 142.12
Sanqi |  |  | KWh | 80597 | 80703 | 106 | 12.87
2016
20th Floor project office meter reading |  |  | KWh

## 23
Daily Utility Consumption Report | [9 empty] | 10002.8
Prepaired by----Ramesh | 2021-05-23 | occupancy | 52% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 30 | Last year same month avg |  | 0% | 0 | 0 | 0
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 189409 | 206316.05 | 16907.05 | 361339.05 | 12000 | 15710.3935
BEST supply |  |  | KVAH | 190825 | 207806.75 | 16981.75 | 363565.75 | 12000 | 15807.2065
Transformer - 1 - 2500KVA |  |  | kwh | 1323735 | 1340135.4 | 16400.4 | 349421.4 | -3807.2065 | 15192.2348
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 16400.4 | 334900.4 | 506.65 | 14560.887
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1680082 | 1680448.935 | 366.935 | 9791.935 | 800 | 425.7363
374.2637
WATER CONSUMPTION
Tankers |  |  | KL | 9 | 8 | 80 | 850 | 65 | 36.9565
BMC |  |  | KL | 139082 | 139142 | 60 | 1330 | 0 | 57.8261 |  | 126171
Total water | [5 empty] | 140 | 2180 | -29.7826 | 94.7826 |  | -12971
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 16981.75 | 9 | 152835.75 | 3272091.75 |  | 142264.8587
C.N.G |  |  | Cu.Mtr | 366.935 | 51.45 | 18878.8058 | 493312.5348 |  | 21448.3711
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 60 | 134 | 8040 | 178220 |  | 7748.6957
Water Tanker |  |  | KL | 80 | 80 | 6400 | 68000
Total cost | [5 empty] | 186154.5558 | 4011624.2848 |  | 174418.4472
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 929336 | 931509.43 | 2173.43 | 45050.43 |  | 1958.7143
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 106.8261
Fire Emergency Power Panel - 1000A |  |  | kwh | 122555 | 123865.51 | 1310.51 | 28640.51 |  | 1245.2396
Main Power Panel -1600A |  |  | kwh | 145272 | 146558.43 | 1286.43 | 26962.43 |  | 1172.2796
Main Lighting and Small power Panel |  |  | kwh | 288057 | 290488.55 | 2431.55 | 43835.55 |  | 1905.8935
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 686 | 686.48 | 0.48 | 686.25 |  | 29.837
Chiller No 1 |  |  | kwh | 240478 | 240478.13 | 0.13 | 58950.13 |  | 2563.0491
Chiller No 2- |  |  | kwh | 59200 | 59198.97 | -1.03 | -1.03 |  | -0.044783
Chiller Water pump Panel- 630A |  |  | kwh | 1021460 | 1023631.6 | 2171.6 | 49673.6 |  | 2159.7217
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 0 | 614 | 614 | 614 |  | 26.6957
Pavilion Power |  |  | kwh | 0 | 187 | 187 | 186.95 |  | 8.1283
Sub Total | [5 empty] | 10174.1 | 257056.31 |  | 11176.3613
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 494190 | 495044.15 | 854.15 | 19569.15 |  | 850.8326
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144639.87 | -0.13 | -0.13 |  | -0.0056522
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 427676 | 428187.11 | 511.11 | 11377.11 |  | 494.657
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 13027 | 13107.96 | 80.96 | 5345.96 |  | 232.433
Chiller No -3 - 1200A |  |  | kwh | 48606 | 54032.61 | 5426.61 | 54032.61 |  | 2349.2439
Chiller No-4 - 1200A |  |  | Kwh | 589514 | 589524.19 | 10.19 | 235.83 |  | 10.2535
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 48560 | 48589.15 | 29.15 | 1872.15 |  | 81.3978
Sub Total | [5 empty] | 6912.04 | 92432.75 | -179.09 | 4018.8152
|  |  | Total TR1 & TR2 |  |  | 17086.14 | 351072.95 | -685.74 | 15264.0413
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419.2 | 20419 | -0.2 | 0.182 |  | 0.007913
5th floor spa |  |  | KWh | 2442 | 2445.87 | 3.87 | 86.87 |  | 3.777
5th Floor |  |  | KWh | 158181 | 158385.74 | 204.74 | 5086.74 |  | 221.1626
12th Floor |  |  | KWh | 159043 | 159251.1 | 208.1 | 4652.1 |  | 202.2652
20th Floor |  |  | KWh | 54311 | 54623.42 | 312.42 | 6052.42 |  | 263.1487
27th Floor |  |  | KWh | 248213 | 248708.17 | 495.17 | 5534.17 |  | 240.6161
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 80703 | 80895.1 | 192.1 | 1901.1 |  | 82.6565
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855741 | 855751 | 10 | 279 |  | 12.1304
Main kitchen power panel no 2 |  |  | KWh | 885899 | 885899 | 0 | 203 |  | 8.8261
Prato kitchen power panel |  |  | KWh | 2526 | 2532.65 | 6.65 | 253.65 |  | 11.0283
San- Qi Indian Kitchen |  |  | KWh | 12148 | 12206.12 | 58.12 | 1236.12 |  | 53.7443
San- Qi Japanese Kitchen |  |  | KWh | 6917 | 6971.3 | 54.3 | 1254.35 |  | 54.537
The club kitchen |  |  | KWh | 702462 | 702500 | 38 | 938 |  | 40.7826
AER Kitchen |  |  | KWh | 672062 | 672189 | 127 | 2164 |  | 94.087
COLD ROOM'S |  |  | KWh | 829800 | 829931 | 131 | 2200 |  | 95.6522
Ball Room 1 kitchen |  |  | KWh | 524389 | 524746.64 | 357.64 | 5285.64 |  | 229.8104
Ball Room 2 kitchen |  |  | KWh | 638140 | 638219.56 | 79.56 | 1741.56 |  | 75.72
B1 Laundry |  |  | kwh | 108014 | 108025.07 | 11.07 | 413.07 |  | 17.9596
STP Electrical |  |  | kwh | 18885 | 19096 | 211 | 4325 |  | 188.0435
Cooling Tower |  |  | kwh | 493529 | 494085 | 556 | 13952 |  | 606.6087
Total | [5 empty] | 1640.34 | 37754.34 |  | 1641.493
MOCK Up Room |  |  | Kwh | 460665 | 460687.56 | 22.56 | 22.56 |  | 0.98087
27th Floor |  |  | Kwh | 81213 | 81219.3 | 6.3 | 6.3 |  | 0.27391
Physic57 |  |  | Kwh | 152683 | 152706.73 | 23.73 | 23.73 |  | 1.0317
Pinoor Legal- Lighting |  |  | Kwh | 64996 | 65034.5 | 38.5 | 38.5 |  | 1.6739
Pinoor Legal- Lighting |  |  | Kwh | 3273.5 | 3273.6 | 0.1 | 0.1 |  | 0.0043478
20th Floor Project office |  |  |  | 27980 | 27986 | 6 | 6
WATER
R.o.plant |  |  | KL | 245099 | 245156 | 57 | 732 |  | 31.8261
STP Water Prod |  |  | KL | 185354 | 185446 | 92 | 1915 |  | 83.2609
Total water Produce |  |  |  | 0 |  | 149 | 2500 |  | 108.6957
Domestic Zone-1 |  |  | KL | 413847 | 413884 | 37 | 998 |  | 43.3913
Domestic Zone-2 |  |  | KL | 102552 | 102567 | 15 | 224 |  | 9.7391
Domestic Zone-3 |  |  | KL | 97749 | 97780 | 31 | 353 |  | 15.3478
Flush Zone -1 |  |  | KL | 149769 | 149790 | 21 | 257 |  | 11.1739
Flush Zone -2 |  |  | KL | 7320 | 7325 | 5 | 140 |  | 6.087
Flush Zone -3 |  |  | KL | 5301 | 5311 | 10 | 173 |  | 7.5217
Total water consum | [5 empty] | 119 | 2145 |  | 93.2609
Water Branches
Branches
Swimming pool |  |  | KL | 7484 | 7484 | 0 | 57 |  | 2.4783
B2 Laundry |  |  | KL | 35906 | 35906 | 0 | 50 |  | 2.1739
Boiler Feed Water |  |  | KL | 19680 | 19682 | 2 | 126 |  | 5.4783
Total |  |  |  | 0 |  | 2 | 191 |  | 8.3043
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62270 | 62330 | 60 | 141 |  | 6.1304
STP flush(new water meter) |  |  | KL | 32459 | 32478 | 19 | 31 |  | 1.3478
Garden Water Pump |  |  | KL | 4527 | 4527 | 0 | 255 |  | 11.087
Total |  |  |  | 0 |  | 79 | 794 |  | 34.5217
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11434 | 11439 | 5 | 5 |  | 0.21739
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8243 | 8254 | 11 | 63 |  | 2.7391
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 4.1304
Total | [5 empty] | 16 | 88 |  | 3.8261
Total Domestic Water (R.O +BMC) |  |  | KL |  |  | 117 | 129 |  | 5.6087
Total Domestic Consumption |  |  | KL |  |  | 98 | 103 |  | 4.4783
Total STP Consumption |  |  | KL |  |  | 79 | 85 |  | 3.6957
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 830512 | 830726.84 | 214.84 | 4638.38 |  | 201.6687
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145905 | 145965.84 | 60.84 | 1278.4 |  | 55.5826
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404.2 | 0.2 | 0.2 |  | 0.0086957
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8970.6 | -0.4 | 0.9 |  | 0.03913
Boiler Gas Consumption | [5 empty] | 91.455 | 1320.455 |  | 57.4111
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40035.1 | 40035.1 | 0 | 288.62 |  | 12.5487
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41637 | 41661.39 | 24.39 | 24 |  | 1.0435
Chiller - 4 |  |  | hr | 32582.93 | 32582.93 | 0 | 13 |  | 0.56522
Steam Boiler -1 |  |  | hr | 22783.45 | 22783.45 | 0 | 43.86 | 24.39 | 1.907
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 8 |  | 0.34783
Steam Boiler -3 |  |  | hr | 70376.65 | 70379.1 | 2.45 | 15 | 2.45 | 0.65217
Hot Water Generator -1 |  |  | hr | 1785.14 | 1793.19 | 8.05 | 176.33 |  | 7.6665
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0052174
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4345.03 | 94435.03 |  | 4105.8709
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 25.7% | 6.0199 |  | 0.26173
Total Chillers Units |  |  | kwh |  |  | 5435.9 | 113217.43 |  | 4922.497
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 32.15% | 7.2162 |  | 0.31375
Total Lighting Units |  |  | kwh |  |  | 2942.66 | 55735.66 |  | 2423.2896
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 17.4% | 3.5498 |  | 0.15434
Total power Units |  |  | Kwh |  |  | 1286.43 | 26962.5 |  | 1172.2826
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.609% | 1.7178 |  | 0.074685
Total mansion power Units |  |  | Kwh |  |  | 854.15 | 22965.15 |  | 998.4848
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.052% | 1.4578 |  | 0.063382
Total fire & em, power Units |  |  | Kwh |  |  | 1310.38 | 28640.38 |  | 1245.2339
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.75% | 1.8281 |  | 0.079481
Lower Basement |  |  | KWh | 37700 | 37780.24 | 80.24
upper basement |  |  | KWh | 91314 | 91687.55 | 373.55
Level 1 |  |  | KWh | 43101 | 43301.7 | 200.7
Level 2 |  |  | KWh | 6493 | 6501.17 | 8.17
2nd floor plant room |  |  | KWh | 20419.2 | 20419 | -0.2
5th floor spa |  |  | KWh | 2442 | 2445.87 | 3.87
5th Floor |  |  | KWh | 158181 | 158385.74 | 204.74
12th Floor |  |  | KWh | 159043 | 159251.1 | 208.1
20th Floor |  |  | KWh | 54311 | 54623.42 | 312.42
27th Floor |  |  | KWh | 248213 | 248708.17 | 495.17
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 80703 | 80895.1 | 192.1
2078.86

## 24
Daily Utility Consumption Report
Prepaired by---Ramesh | 2020-05-24 | occupancy | 63% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 28 | Last year same month avg |  | 0% | 0 | 0 | 0
|  | humidity | 80%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 206316.05 | 222863.67 | 16547.62 | 377886.67 | 12000 | 15745.2779
BEST supply |  |  | KVAH | 207806.75 | 224411.63 | 16604.88 | 380170.63 | 12000 | 15840.4429
Transformer - 1 - 2500KVA |  |  | kwh | 1340135.4 | 1356145.2 | 16009.8 | 365431.2 | -3840.4429 | 15226.3
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0 | 1643044-1655344
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 16009.8 | 350910.2 | 537.82 | 14621.2583
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1680448.935 | 1680959.63 | 510.695 | 10302.63 | 800 | 429.2762
370.7238
WATER CONSUMPTION | [6 empty] | 0
Tankers |  |  | KL | 8 | 5 | 50 | 900 | 65 | 37.5
BMC |  |  | KL | 139142 | 139202 | 60 | 1390 |  | 57.9167
Total water | [5 empty] | 110 | 2290 | -30.4167 | 95.4167
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 16604.88 | 9 | 149443.92 | 3421535.67 |  | 142563.9862
C.N.G |  |  | Cu.Mtr | 510.695 | 51.45 | 26275.2577 | 519587.7925 |  | 21649.4914
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 60 | 134 | 8040 | 186260 |  | 7760.8333
Water Tanker |  |  | KL | 50 | 80 | 4000 | 72000
Total cost | [5 empty] | 187759.1777 | 4199383.4625 |  | 174974.3109
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 931509.43 | 933635.91 | 2126.48 | 47176.91 |  | 1965.7046
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 102.375
Fire Emergency Power Panel - 1000A |  |  | kwh | 123865.51 | 125152.88 | 1287.37 | 29927.88 |  | 1246.995
Main Power Panel -1600A |  |  | kwh | 146558.43 | 147796.71 | 1238.28 | 28200.71 |  | 1175.0296
Main Lighting and Small power Panel |  |  | kwh | 290488.55 | 292734.51 | 2245.96 | 46081.51 |  | 1920.0629 |  | 772.8
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 686.48 | 686.48 | 0 | 686.25 |  | 28.5938
Chiller No 1 |  |  | kwh | 240478.13 | 240478.13 | 0 | 58950.13 |  | 2456.2554
Chiller No 2- |  |  | kwh | 59198.97 | 59198.97 | 0 | -1.03 |  | -0.042917
Chiller Water pump Panel- 630A |  |  | kwh | 1023631.6 | 1025857.8 | 2226.2 | 51899.8 |  | 2162.4917
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 614 |  | 25.5833
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 186.95 |  | 7.7896
Sub Total | [5 empty] | 9124.29 | 266180.6 |  | 11090.8583
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 495044.15 | 495908.59 | 864.44 | 20433.59 |  | 851.3996
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144639.87 | 0 | -0.13 |  | -0.0054167
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 428187.11 | 428706.03 | 518.92 | 11896.03 |  | 495.6679
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 13107.96 | 13189.91 | 81.95 | 5427.91 |  | 226.1629
Chiller No -3 - 1200A |  |  | kwh | 54032.61 | 59204.73 | 5172.12 | 59204.73 |  | 2466.8637
Chiller No-4 - 1200A |  |  | Kwh | 589524.19 | 589534.11 | 9.92 | 245.75 |  | 10.2396
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 48589.15 | 48687.37 | 98.22 | 1970.37 |  | 82.0988
Sub Total | [5 empty] | 6745.57 | 99178.32 | 677.76 | 4132.43
|  |  | Total TR1 & TR2 |  |  | 15869.86 | 366942.81 | 139.94 | 15289.2838
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.182 |  | 0.0075833
5th floor spa |  |  | KWh | 2445.87 | 2449.72 | 3.85 | 90.72 |  | 3.78
5th Floor |  |  | KWh | 158385.74 | 158599.99 | 214.25 | 5300.99 |  | 220.8746
12th Floor |  |  | KWh | 159251.1 | 159470.85 | 219.75 | 4871.85 |  | 202.9938
20th Floor |  |  | KWh | 54623.42 | 54926.18 | 302.76 | 6355.18 |  | 264.7992
27th Floor |  |  | KWh | 248708.17 | 249138.4 | 430.23 | 5964.4 |  | 248.5167
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 80895.1 | 80980.38 | 85.28 | 1986.38 |  | 82.7658
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855751 | 855760 | 9 | 288 |  | 12
Main kitchen power panel no 2 |  |  | KWh | 885899 | 885901 | 2 | 205 |  | 8.5417
Prato kitchen power panel |  |  | KWh | 2532.65 | 2539.68 | 7.03 | 260.68 |  | 10.8617
San- Qi Indian Kitchen |  |  | KWh | 12206.12 | 12264.21 | 58.09 | 1294.21 |  | 53.9254
San- Qi Japanese Kitchen |  |  | KWh | 6971.3 | 7028.83 | 57.53 | 1311.88 |  | 54.6617
The club kitchen |  |  | KWh | 702500 | 702542 | 42 | 980 |  | 40.8333
AER Kitchen |  |  | KWh | 672189 | 672281 | 92 | 2256 |  | 94
COLD ROOM'S |  |  | KWh | 829931 | 830054 | 123 | 2323 |  | 96.7917
Ball Room 1 kitchen |  |  | KWh | 524746.64 | 525089.04 | 342.4 | 5628.04 |  | 234.5017
Ball Room 2 kitchen |  |  | KWh | 638219.56 | 638300.04 | 80.48 | 1822.04 |  | 75.9183
B1 Laundry |  |  | kwh | 108025.07 | 108055.15 | 30.08 | 443.15 |  | 18.4646
STP Electrical |  |  | kwh | 19096 | 19231 | 135 | 4460 |  | 185.8333
Cooling Tower |  |  | kwh | 494085 | 494738 | 653 | 14605 |  | 608.5417
Total |  |  |  | 0 |  | 1631.61 | 39385.95 |  | 1641.0813
MOCK Up Room |  |  | Kwh | 460687.56 | 460712.84 | 25.28 | 25.28 |  | 1.0533
27th Floor |  |  | Kwh | 81219.3 | 81237.3 | 18 | 18 |  | 0.75
Physic57 |  |  | Kwh | 152706.73 | 152832.03 | 125.3 | 125.3 |  | 5.2208
Pinoor Legal- Lighting |  |  | Kwh | 65034.5 | 65080.1 | 45.6 | 45.6 |  | 1.9
Pinoor Legal- Lighting |  |  | Kwh | 3273.6 | 3273.6 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27986 | 27986.7 | 0.7 | 0.7
WATER
R.o.plant |  |  | KL | 245156 | 245184 | 28 | 760 |  | 31.6667
STP Water Prod |  |  | KL | 185446 | 185520 | 74 | 1989 |  | 82.875
Total water Produce |  |  |  | 0 |  | 102 | 2602 |  | 108.4167
Domestic Zone-1 |  |  | KL | 413884 | 413924 | 40 | 1038 |  | 43.25
Domestic Zone-2 |  |  | KL | 102567 | 102578 | 11 | 235 |  | 9.7917
Domestic Zone-3 |  |  | KL | 97780 | 97796 | 16 | 369 |  | 15.375
Flush Zone -1 |  |  | KL | 149790 | 149818 | 28 | 285 |  | 11.875
Flush Zone -2 |  |  | KL | 7325 | 7328 | 3 | 143 |  | 5.9583
Flush Zone -3 |  |  | KL | 5311 | 5325 | 14 | 187 |  | 7.7917
Total water consum | [5 empty] | 112 | 2257 |  | 94.0417
Water Branches
Branches
Swimming pool |  |  | KL | 7484 | 7484 | 0 | 57 |  | 2.375
B2 Laundry |  |  | KL | 35906 | 35907 | 1 | 51 |  | 2.125
Boiler Feed Water |  |  | KL | 19682 | 19685 | 3 | 127 |  | 5.2917
Total | [5 empty] | 4 | 193 |  | 8.0417
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62330 | 62370 | 40 | 121 |  | 5.0417
STP flush(new water meter) |  |  | KL | 32478 | 32518 | 40 | 52 |  | 2.1667
Garden Water Pump |  |  | KL | 4527 | 4527 | 0 | 255 |  | 10.625
Total |  |  |  | 0 |  | 80 | 795 |  | 33.125
Flushing Water | [8 empty] | 0
Flush Zone 2 pump meter |  |  | KL | 11439 | 11444 | 5 | 5 |  | 0.20833
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8254 | 8261 | 7 | 59 |  | 2.4583
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 3.9583
Total | [5 empty] | 12 | 84 |  | 3.5
Total Domestic Water (R.O +BMC) |  |  | KL |  |  | 88 | 100 |  | 4.1667
Total Domestic Consumption |  |  | KL |  |  | 84 | 89 |  | 3.7083
Total STP Consumption |  |  | KL |  |  | 80 | 86 |  | 3.5833
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 830726.84 | 830957 | 230.16 | 4868.54 |  | 202.8558
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 145965.84 | 146037.63 | 71.79 | 1350.19 |  | 56.2579
Sanqi IndianGas meter Reading |  |  | m3 | 31404.2 | 31404.2 | 0 | 0.2 |  | 0.0083333
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970.6 | 8970.6 | 0 | 0.9 |  | 0.0375
Boiler Gas Consumption | [5 empty] | 208.745 | 1529.2 |  | 63.7167
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40035.1 | 40059.1 | 24 | 312.62 |  | 13.0258
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 24 | 0
Chiller - 3 |  |  | hr | 41661.39 | 41661.39 | 0 | 24 |  | 1
Chiller - 4 |  |  | hr | 32582.93 | 32582.93 | 0 | 13 |  | 0.54167
Steam Boiler -1 |  |  | hr | 22783.45 | 22783.45 | 0 | 43.86 | 0 | 1.8275
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 8 |  | 0.33333
Steam Boiler -3 |  |  | hr | 70379.1 | 70389.35 | 10.25 | 25.25 | 10.25 | 1.0521
Hot Water Generator -1 |  |  | hr | 1793.19 | 1801.71 | 8.52 | 184.85 |  | 7.7021
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.58 | -0.3 | -0.42 |  | -0.0175
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4352.68 | 98787.71 |  | 4116.1546
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 26.3% | 6.2829 |  | 0.26179
Total Chillers Units |  |  | kwh |  |  | 5182.04 | 118399.47 |  | 4933.3113
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 31.32% | 7.5293 |  | 0.31372
Total Lighting Units |  |  | kwh |  |  | 2764.88 | 58500.54 |  | 2437.5225
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 16.71% | 3.7169 |  | 0.15487
Total power Units |  |  | Kwh |  |  | 1238.28 | 28200.78 |  | 1175.0325
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.483% | 1.7926 |  | 0.074691
Total mansion power Units |  |  | Kwh |  |  | 864.44 | 23829.59 |  | 992.8996
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.224% | 1.51 |  | 0.062918
Total fire & em, power Units |  |  | Kwh |  |  | 1287.37 | 29927.75 |  | 1246.9896
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.78% | 1.9059 |  | 0.079411
Lower Basement |  |  | KWh | 37780.24 | 37863.18 | 82.94
upper basement |  |  | KWh | 91687.55 | 92088.62 | 401.07
Level 1 |  |  | KWh | 43301.7 | 43511.01 | 209.31
Level 2 |  |  | KWh | 6501.17 | 6509.7 | 8.53
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2445.87 | 2449.72 | 3.85
5th Floor |  |  | KWh | 158385.74 | 158599.99 | 214.25
12th Floor |  |  | KWh | 159251.1 | 159470.85 | 219.75
20th Floor |  |  | KWh | 54623.42 | 54926.18 | 302.76
27th Floor |  |  | KWh | 248708.17 | 249138.4 | 430.23
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 80895.1 | 80980.38 | 85.28
1957.97

## 25
Daily Utility Consumption Report
Prepaired by- Ramesh | 2020-05-25 | occupancy | 54% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 31 | Last year same month avg |  | 0% | 0 | 0 | 0
|  | humidity | 80%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 222863.67 | 239099.07 | 16235.4 | 394122.07 | 12000 | 15764.8828 |  |  | 0.9961
BEST supply |  |  | KVAH | 224411.63 | 240710.67 | 16299.04 | 396469.67 | 12000 | 15858.7868 | 1375467 | 1667461
Transformer - 1 - 2500KVA |  |  | kwh | 1356145.2 | 1371859.3 | 15714.1 | 381145.3 | -3858.7868 | 15245.812
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0 |  | 291994
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0 |  |  | 16172.0085
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 15714.1 | 366624.3 | 521.3 | 14664.972 |  | -102128.07
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1680959.63 | 1681634.919 | 675.289 | 10977.919 | 800 | 439.1168
[8 empty] | 360.8832 |  |  |  |  | -410
WATER CONSUMPTION | [12 empty] | -1230
Tankers |  |  | KL | 5 | 6 | 60 | 960 | 65 | 38.4
BMC |  |  | KL | 139202 | 139262 | 60 | 1450 |  | 58
Total water | [5 empty] | 120 | 2410 | -31.4 | 96.4
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 16299.04 | 9 | 146691.36 | 3568227.03 |  | 142729.0812
C.N.G |  |  | Cu.Mtr | 675.289 | 51.45 | 34743.6191 | 554331.4115 |  | 22173.2565
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 60 | 134 | 8040 | 194300 |  | 7772
Water Tanker |  |  | KL | 60 | 80 | 4800 | 76800
Total cost | [5 empty] | 194274.9791 | 4393658.4416 |  | 175746.3377 |  |  |  | 1020
BRANCH READINGS & CONSUMPTION | [12 empty] | 340
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 933635.91 | 935746.79 | 2110.88 | 49287.79 |  | 1971.5116
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 98.28
Fire Emergency Power Panel - 1000A |  |  | kwh | 125152.88 | 126400.73 | 1247.85 | 31175.73 |  | 1247.0292
Main Power Panel -1600A |  |  | kwh | 147796.71 | 149009.04 | 1212.33 | 29413.04 |  | 1176.5216
Main Lighting and Small power Panel |  |  | kwh | 292734.51 | 294778.27 | 2043.76 | 48125.27 |  | 1925.0108
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 686.48 | 686.48 | 0 | 686.25 |  | 27.45
Chiller No 1 |  |  | kwh | 240478.13 | 240478.13 | 0 | 58950.13 |  | 2358.0052
Chiller No 2- |  |  | kwh | 59198.97 | 59198.97 | 0 | -1.03 |  | -0.0412
Chiller Water pump Panel- 630A |  |  | kwh | 1025857.8 | 1028056.5 | 2198.7 | 54098.5 |  | 2163.94
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 614 |  | 24.56
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 186.95 |  | 7.478
Sub Total | [5 empty] | 8813.52 | 274994.12 |  | 10999.7648
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 495908.59 | 496769.11 | 860.52 | 21294.11 |  | 851.7644
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144639.87 | 0 | -0.13 |  | -0.0052
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 428706.03 | 429230.87 | 524.84 | 12420.87 |  | 496.8348
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 13189.91 | 13269.62 | 79.71 | 5507.62 |  | 220.3048
Chiller No -3 - 1200A |  |  | kwh | 59204.73 | 64199.47 | 4994.74 | 64199.47 |  | 2567.9788
Chiller No-4 - 1200A |  |  | Kwh | 589534.11 | 589543.71 | 9.6 | 255.35 |  | 10.214
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 48687.37 | 48931.51 | 244.14 | 2214.51 |  | 88.5804
Sub Total | [5 empty] | 6713.55 | 105891.87 | 708.33 | 4235.6748
|  |  | Total TR1 & TR2 |  |  | 15527.07 | 382469.88 | 187.03 | 15298.7952
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.182 |  | 0.00728
5th floor spa |  |  | KWh | 2449.72 | 2453.47 | 3.75 | 94.47 |  | 3.7788
5th Floor |  |  | KWh | 158599.99 | 158798.06 | 198.07 | 5499.06 |  | 219.9624
12th Floor |  |  | KWh | 159470.85 | 159730 | 259.15 | 5131 |  | 205.24
20th Floor |  |  | KWh | 54926.18 | 55178.79 | 252.61 | 6607.79 |  | 264.3116
27th Floor |  |  | KWh | 249138.4 | 249501.01 | 362.61 | 6327.01 |  | 253.0804
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 80980.38 | 81051.97 | 71.59 | 2057.97 |  | 82.3188
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855760 | 855769 | 9 | 297 |  | 11.88
Main kitchen power panel no 2 |  |  | KWh | 885901 | 885915 | 14 | 219 |  | 8.76
Prato kitchen power panel |  |  | KWh | 2539.68 | 2545.79 | 6.11 | 266.79 |  | 10.6716
San- Qi Indian Kitchen |  |  | KWh | 12264.21 | 12318.61 | 54.4 | 1348.61 |  | 53.9444
San- Qi Japanese Kitchen |  |  | KWh | 7028.83 | 7085.85 | 57.02 | 1368.9 |  | 54.756
The club kitchen |  |  | KWh | 702542 | 702588 | 46 | 1026 |  | 41.04
AER Kitchen |  |  | KWh | 672281 | 672382 | 101 | 2357 |  | 94.28
COLD ROOM'S |  |  | KWh | 830054 | 830175 | 121 | 2444 |  | 97.76
Ball Room 1 kitchen |  |  | KWh | 525089.04 | 525454.12 | 365.08 | 5993.12 |  | 239.7248
Ball Room 2 kitchen |  |  | KWh | 638300.04 | 638389.16 | 89.12 | 1911.16 |  | 76.4464
B1 Laundry |  |  | kwh | 108055.15 | 108065.74 | 10.59 | 453.74 |  | 18.1496 |  |  | 367.29
STP Electrical |  |  | kwh | 19231 | 19414 | 183 | 4643 |  | 185.72
Cooling Tower |  |  | kwh | 494738 | 495387 | 649 | 15254 |  | 610.16
Total | [5 empty] | 1705.32 | 41091.27 |  | 1643.6508
MOCK Up Room |  |  | Kwh | 460712.84 | 460736.84 | 24 | 24 |  | 0.96 |  |  | 24.1206
27th Floor |  |  | Kwh | 81237.3 | 81270.7 | 33.4 | 33.4 |  | 1.336
Physic57 |  |  | Kwh | 152832.03 | 152855.96 | 23.93 | 23.93 |  | 0.9572
Pinoor Legal- Lighting |  |  | Kwh | 65080.1 | 65110 | 29.9 | 29.9 |  | 1.196 |  |  | 0.99512
Pinoor Legal- Lighting |  |  | Kwh | 3273.6 | 3273.6 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27986.7 | 27990 | 3.3 | 3.3
WATER
R.o.plant |  |  | KL | 245184 | 245238 | 54 | 814 |  | 32.56
STP Water Prod |  |  | KL | 185520 | 185617 | 97 | 2086 |  | 83.44
Total water Produce |  |  |  | 0 |  | 151 | 2753 |  | 110.12
Domestic Zone-1 |  |  | KL | 413924 | 414002 | 78 | 1116 |  | 44.64
Domestic Zone-2 |  |  | KL | 102578 | 102587 | 9 | 244 |  | 9.76
Domestic Zone-3 |  |  | KL | 97796 | 97809 | 13 | 382 |  | 15.28
Flush Zone -1 |  |  | KL | 149818 | 149825 | 7 | 292 |  | 11.68
Flush Zone -2 |  |  | KL | 7328 | 7334 | 6 | 149 |  | 5.96
Flush Zone -3 |  |  | KL | 5325 | 5341 | 16 | 203 |  | 8.12
Total water consum | [5 empty] | 129 | 2386 |  | 95.44
Water Branches
Branches
Swimming pool |  |  | KL | 7484 | 7484 | 0 | 57 |  | 2.28
B2 Laundry |  |  | KL | 35907 | 35923 | 16 | 66 |  | 2.64
Boiler Feed Water |  |  | KL | 19685 | 19685 | 0 | 124 |  | 4.96
Total |  |  |  | 0 |  | 16 | 205 |  | 8.2
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62370 | 62420 | 50 | 131 |  | 5.24
STP flush(new water meter) |  |  | KL | 32518 | 32518 | 0 | 12 |  | 0.48
Garden Water Pump |  |  | KL | 4527 | 4543 | 16 | 271 |  | 10.84
Total |  |  |  | 0 |  | 66 | 781 |  | 31.24
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11444 | 11452 | 8 | 8 |  | 0.32
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8261 | 8273 | 12 | 64 |  | 2.56
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 3.8
Total | [5 empty] | 20 | 92 |  | 3.68
Total Domestic Water (R.O +BMC) |  |  | KL |  |  | 114 | 126 |  | 5.04
Total Domestic Consumption |  |  | KL |  |  | 122 | 127 |  | 5.08
Total STP Consumption |  |  | KL |  |  | 66 | 72 |  | 2.88
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 830957 | 831165.4 | 208.4 | 5076.94 |  | 203.0776
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 146037.63 | 146111.75 | 74.12 | 1424.31 |  | 56.9724
Sanqi IndianGas meter Reading |  |  | m3 | 31404.2 | 31404.2 | 0 | 0.2 |  | 0.008
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970.6 | 8970.6 | 0 | 0.9 |  | 0.036
Boiler Gas Consumption | [5 empty] | 392.769 | 1921.969 |  | 76.8788
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40059.1 | 40059.1 | 0 | 312.62 |  | 12.5048 |  |  |  |  | 25
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41661.39 | 41685.3 | 23.91 | 47.91 |  | 1.9164
Chiller - 4 |  |  | hr | 32582.93 | 32582.93 | 0 | 13 |  | 0.52
Steam Boiler -1 |  |  | hr | 22783.45 | 22791.35 | 7.9 | 51.76 | 31.81 | 2.0704
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.73 | 0.01 | 8.01 |  | 0.3204
Steam Boiler -3 |  |  | hr | 70389.35 | 70389.35 | 0 | 25.25 | 0.01 | 1.01
Hot Water Generator -1 |  |  | hr | 1801.71 | 1809.4 | 7.69 | 192.54 |  | 7.7016
Hot Water Generator -2 |  |  | hr | 4636.58 | 4636.88 | 0.3 | -0.12 |  | -0.0048
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4309.58 | 103097.29 |  | 4123.8916
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 26.54% | 6.5483 |  | 0.26193
Total Chillers Units |  |  | kwh |  |  | 5004.34 | 123403.81 |  | 4936.1524
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 30.82% | 7.8376 |  | 0.3135
Total Lighting Units |  |  | kwh |  |  | 2568.6 | 61069.14 |  | 2442.7656
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 15.82% | 3.8751 |  | 0.155
Total power Units |  |  | Kwh |  |  | 1212.33 | 29413.11 |  | 1176.5244
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.467% | 1.8673 |  | 0.07469
Total mansion power Units |  |  | Kwh |  |  | 860.52 | 24690.11 |  | 987.6044
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.3% | 1.563 |  | 0.062521
Total fire & em, power Units |  |  | Kwh |  |  | 1247.85 | 31175.6 |  | 1247.024
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.686% | 1.9827 |  | 0.079309
Lower Basement |  |  | KWh | 37863.18 | 37945.34 | 82.16
upper basement |  |  | KWh | 92088.62 | 92482.99 | 394.37
Level 1 |  |  | KWh | 43511.01 | 43713.43 | 202.42
Level 2 |  |  | KWh | 6509.7 | 6516.74 | 7.04
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2449.72 | 2453.47 | 3.75
5th Floor |  |  | KWh | 158599.99 | 158798.06 | 198.07
12th Floor |  |  | KWh | 159470.85 | 159730 | 259.15
20th Floor |  |  | KWh | 54926.18 | 55178.79 | 252.61
27th Floor |  |  | KWh | 249138.4 | 249501.01 | 362.61
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 80980.38 | 81051.97 | 71.59
1833.77

## 26
Daily Utility Consumption Report
Prepaired by-- Ramesh | 2020-04-26 | occupancy | 54% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 28 | Last year same month avg
|  | humidity | 74%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 239099.07 | 258323.63 | 19224.56 | 413346.63 | 12000 | 15897.9473
BEST supply |  |  | KVAH | 240710.67 | 260072.39 | 19361.72 | 415831.39 | 12000 | 15993.515
Transformer - 1 - 2500KVA |  |  | kwh | 1371859.3 | 1390471.6 | 18612.3 | 399757.6 | -3993.515 | 15375.2923
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0 | 1375467
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 18612.3 | 385236.6 | 612.26 | 14816.7923
GAS CONSUMPTION | [9 empty] | 1679344
Gas consumption |  |  | m3 | 1681634.919 | 1682009 | 374.081 | 11352 | 800 | 436.6154
[8 empty] | 363.3846 |  | 303877
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 6 | 60 | 1020 | 65 | 39.2308
BMC |  |  | KL | 139262 | 139315 | 53 | 1503 |  | 57.8077 | 11687.5769
Total water | [5 empty] | 113 | 2523 | -32.0385 | 97.0385
DIESEL CONSUMPTION | [9 empty] | #REF!
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 19361.72 | 9 | 174255.48 | 3742482.51 |  | 143941.635
C.N.G |  |  | Cu.Mtr | 374.081 | 51.45 | 19246.4675 | 573577.879 |  | 22060.6877
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 53 | 134 | 7102 | 201402 |  | 7746.2308
Water Tanker |  |  | KL | 60 | 80 | 4800 | 81600
Total cost | [5 empty] | 205403.9475 | 4599062.389 |  | 176887.015
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 935746.79 | 938391.75 | 2644.96 | 51932.75 |  | 1997.4135
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 94.5
Fire Emergency Power Panel - 1000A |  |  | kwh | 126400.73 | 127744.73 | 1344 | 32519.73 |  | 1250.7588
Main Power Panel -1600A |  |  | kwh | 149009.04 | 150235.39 | 1226.35 | 30639.39 |  | 1178.4381
Main Lighting and Small power Panel |  |  | kwh | 294778.27 | 296927.47 | 2149.2 | 50274.47 |  | 1933.6335
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 686.48 | 888.99 | 202.51 | 888.76 |  | 34.1831
Chiller No 1 |  |  | kwh | 240478.13 | 240478.13 | 0 | 58950.13 |  | 2267.3127
Chiller No 2- |  |  | kwh | 59198.97 | 59198.97 | 0 | -1.03 |  | -0.039615 |  | 3450
Chiller Water pump Panel- 630A |  |  | kwh | 1028056.5 | 1030659.3 | 2602.8 | 56701.3 |  | 2180.8192
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 614 |  | 23.6154
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 186.95 |  | 7.1904
Sub Total | [5 empty] | 10169.82 | 285163.94 |  | 10967.8438
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 496769.11 | 498182.83 | 1413.72 | 22707.83 |  | 873.3781
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144639.87 | 0 | -0.13 |  | -0.005
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 429230.87 | 429772.55 | 541.68 | 12962.55 |  | 498.5596
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 13269.62 | 13353 | 83.38 | 5591 |  | 215.0385
Chiller No -3 - 1200A |  |  | kwh | 64199.47 | 68110.68 | 3911.21 | 68110.68 |  | 2619.6415
Chiller No-4 - 1200A |  |  | Kwh | 589543.71 | 591627.75 | 2084.04 | 2339.39 |  | 89.9765
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 48931.51 | 48968.68 | 37.17 | 2251.68 |  | 86.6031
Sub Total | [5 empty] | 8071.2 | 113963.07 | 983.54 | 4383.195
|  |  | Total TR1 & TR2 |  |  | 18241.02 | 400710.9 | 371.28 | 15411.9577
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.182 |  | 0.007
5th floor spa |  |  | KWh | 2453.47 | 2457.1 | 3.63 | 98.1 |  | 3.7731
5th Floor |  |  | KWh | 158798.06 | 158972.7 | 174.64 | 5673.7 |  | 218.2192
12th Floor |  |  | KWh | 159730 | 159915.88 | 185.88 | 5316.88 |  | 204.4954
20th Floor |  |  | KWh | 55178.79 | 55424.42 | 245.63 | 6853.42 |  | 263.5931
27th Floor |  |  | KWh | 249501.01 | 249886.57 | 385.56 | 6712.57 |  | 258.1758
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 81051.97 | 81191.51 | 139.54 | 2197.51 |  | 84.5196
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855769 | 855782 | 13 | 310 |  | 11.9231
Main kitchen power panel no 2 |  |  | KWh | 885915 | 885932 | 17 | 236 |  | 9.0769
Prato kitchen power panel |  |  | KWh | 2545.79 | 2553.07 | 7.28 | 274.07 |  | 10.5412
San- Qi Indian Kitchen |  |  | KWh | 12318.61 | 12387.5 | 68.89 | 1417.5 |  | 54.5192
San- Qi Japanese Kitchen |  |  | KWh | 7085.85 | 7139 | 53.15 | 1422.05 |  | 54.6942
The club kitchen |  |  | KWh | 702588 | 702629 | 41 | 1067 |  | 41.0385
AER Kitchen |  |  | KWh | 672382 | 672391 | 9 | 2366 |  | 91
COLD ROOM'S |  |  | KWh | 830175 | 830307 | 132 | 2576 |  | 99.0769
Ball Room 1 kitchen |  |  | KWh | 525454.12 | 525838.04 | 383.92 | 6377.04 |  | 245.2708
Ball Room 2 kitchen |  |  | KWh | 638389.16 | 638467.72 | 78.56 | 1989.72 |  | 76.5277
B1 Laundry |  |  | kwh | 108065.74 | 108076.42 | 10.68 | 464.42 |  | 17.8623
STP Electrical |  |  | kwh | 19414 | 19604 | 190 | 4833 |  | 185.8846
Cooling Tower |  |  | kwh | 495387 | 496173 | 786 | 16040 |  | 616.9231
Total |  |  |  | 0 |  | 1790.48 | 42881.75 |  | 1649.2981
MOCK Up Room |  |  | Kwh | 460736.84 | 460767.32 | 30.48 | 30.48 |  | 1.1723
27th Floor |  |  | Kwh | 81270.7 | 81289.5 | 18.8 | 18.8 |  | 0.72308
Physic57 |  |  | Kwh | 152855.96 | 152878.01 | 22.05 | 22.05 |  | 0.84808
Pinoor Legal- Lighting |  |  | Kwh | 65110 | 65120.4 | 10.4 | 10.4 |  | 0.4
Pinoor Legal- Lighting |  |  | Kwh | 3273.6 | 3273.6 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 27990 | 28000.92 | 10.92 | 10.92
WATER
R.o.plant |  |  | KL | 245238 | 245276 | 38 | 852 |  | 32.7692
STP Water Prod |  |  | KL | 185617 | 185696 | 79 | 2165 |  | 83.2692
Total water Produce |  |  |  | 0 |  | 117 | 2870 |  | 110.3846
Domestic Zone-1 |  |  | KL | 414002 | 414045 | 43 | 1159 |  | 44.5769
Domestic Zone-2 |  |  | KL | 102587 | 102596 | 9 | 253 |  | 9.7308
Domestic Zone-3 |  |  | KL | 97809 | 97827 | 18 | 400 |  | 15.3846
Flush Zone -1 |  |  | KL | 149825 | 149830 | 5 | 297 |  | 11.4231
Flush Zone -2 |  |  | KL | 7334 | 7338 | 4 | 153 |  | 5.8846
Flush Zone -3 |  |  | KL | 5341 | 5347 | 6 | 209 |  | 8.0385
Total water consum | [5 empty] | 85 | 2471 |  | 95.0385
Water Branches
Branches
Swimming pool |  |  | KL | 7484 | 7484 | 0 | 57 |  | 2.1923
B2 Laundry |  |  | KL | 35923 | 35924 | 1 | 51 |  | 1.9615
Boiler Feed Water |  |  | KL | 19685 | 19692 | 7 | 131 |  | 5.0385
Total |  |  |  | 0 |  | 8 | 197 |  | 7.5769
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62420 | 62518 | 98 | 179 |  | 6.8846
STP flush(new water meter) |  |  | KL | 32518 | 32542 | 24 | 36 |  | 1.3846
Garden Water Pump |  |  | KL | 4543 | 4543 | 0 | 255 |  | 9.8077
Total |  |  |  | 0 |  | 122 | 837 |  | 32.1923
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11452 | 11457 | 5 | 5 |  | 0.19231
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8273 | 8279 | 6 | 58 |  | 2.2308
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 3.6538
Total | [5 empty] | 11 | 83 |  | 3.1923
Total Domestic Water (R.O +BMC) |  |  | KL |  |  | 91 | 103 |  | 3.9615
Total Domestic Consumption |  |  | KL |  |  | 80 | 85 |  | 3.2692
Total STP Consumption |  |  | KL |  |  | 122 | 128 |  | 4.9231
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 831165.4 | 831372.91 | 207.51 | 5284.45 |  | 203.2481
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 146111.75 | 146182.97 | 71.22 | 1495.53 |  | 57.5204
Sanqi IndianGas meter Reading |  |  | m3 | 31404.2 | 31404.2 | 0 | 0.2 |  | 0.0076923
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970.6 | 8970.6 | 0 | 0.9 |  | 0.034615
Boiler Gas Consumption | [5 empty] | 95.351 | 2017.32 |  | 77.5892
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40059.1 | 40059.1 | 0 | 312.62 |  | 12.0238
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41706.3 | 41730.34 | 24.04 | 71.95 |  | 2.7673
Chiller - 4 |  |  | hr | 32582.93 | 32595 | 12.07 | 25.07 |  | 0.96423
Steam Boiler -1 |  |  | hr | 22791.35 | 22791.36 | 0.01 | 51.77 | 36.12 | 1.9912
Steam Boiler -2 |  |  | hr | 25051.73 | 25051.72 | -0.01 | 8 |  | 0.30769
Steam Boiler -3 |  |  | hr | 70389.35 | 70392.18 | 2.83 | 28.08 | 2.82 | 1.08
Hot Water Generator -1 |  |  | hr | 1809.4 | 1817.18 | 7.78 | 200.32 |  | 7.7046
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0046154
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 5247.76 | 108345.05 |  | 4167.1173
% of HVAC units of Total Con.(LT) |  |  | % |  | 0.04 | 27.3% | 6.8213 |  | 0.26236
Total Chillers Units |  |  | kwh |  |  | 5995.25 | 129399.06 |  | 4976.8869
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 31.19% | 8.1494 |  | 0.31344
Total Lighting Units |  |  | kwh |  |  | 2690.88 | 63760.02 |  | 2452.3085
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 14% | 4.0151 |  | 0.15443
Total power Units |  |  | Kwh |  |  | 1226.35 | 30639.46 |  | 1178.4408
% of power Units of Total Con.(LT) |  |  | % |  |  | 6.379% | 1.931 |  | 0.074271
Total mansion power Units |  |  | Kwh |  |  | 1413.72 | 26103.83 |  | 1003.9935
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 7.354% | 1.6366 |  | 0.062945
Total fire & em, power Units |  |  | Kwh |  |  | 1344 | 32519.6 |  | 1250.7538
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 6.991% | 2.0526 |  | 0.078948
Lower Basement |  |  | KWh | 37945.34 | 38024.69 | 79.35
upper basement |  |  | KWh | 92482.99 | 92856.51 | 373.52
Level 1 |  |  | KWh | 43713.43 | 43914 | 200.57
Level 2 |  |  | KWh | 6516.74 | 6525.9 | 9.16
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2453.47 | 2457.1 | 3.63
5th Floor |  |  | KWh | 158798.06 | 158972.7 | 174.64
12th Floor |  |  | KWh | 159730 | 159915.88 | 185.88
20th Floor |  |  | KWh | 55178.79 | 55424.42 | 245.63
27th Floor |  |  | KWh | 249501.01 | 249886.57 | 385.56
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 81051.97 | 81191.51 | 139.54
1797.48

## 27
Daily Utility Consumption Report
Prepaired by-- Nilesh | 2020-05-27 | occupancy | 70% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 30 | Last year same month avg
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 258323.63 | 275096 | 16772.37 | 430119 | 12000 | 15930.3333 | 1375467 | 1691553 | 316086
BEST supply |  |  | KVAH | 260072.39 | 276912 | 16839.61 | 432671 | 12000 | 16024.8519
Transformer - 1 - 2500KVA |  |  | kwh | 1390471.6 | 1406705 | 16233.4 | 415991 | -4024.8519 | 15407.0741
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 16233.4 | 401470 | 538.97 | 14869.2593
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1682009 | 1682624 | 615 | 11967 | 800 | 443.2222
356.7778
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 6 | 60 | 1080 | 65 | 40
BMC |  |  | KL | 139315 | 139376 | 61 | 1564 |  | 57.9259
Total water | [5 empty] | 121 | 2644 | -32.9259 | 97.9259
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 16839.61 | 9 | 151556.49 | 3894039 |  | 144223.6667
C.N.G |  |  | Cu.Mtr | 615 | 51.45 | 31641.75 | 605219.629 |  | 22415.5418
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 61 | 134 | 8174 | 209576 |  | 7762.0741
Water Tanker |  |  | KL | 60 | 80 | 4800 | 86400
Total cost | [5 empty] | 196172.24 | 4795234.629 |  | 177601.2826
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 938391.75 | 940873 | 2481.25 | 54414 |  | 2015.3333
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 91
Fire Emergency Power Panel - 1000A |  |  | kwh | 127744.73 | 129041 | 1296.27 | 33816 |  | 1252.4444
Main Power Panel -1600A |  |  | kwh | 150235.39 | 151412 | 1176.61 | 31816 |  | 1178.3704
Main Lighting and Small power Panel |  |  | kwh | 296927.47 | 299149 | 2221.53 | 52496 |  | 1944.2963
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 888.99 | 889 | 0.01 | 888.77 |  | 32.9174
Chiller No 1 |  |  | kwh | 240478.13 | 240478 | -0.13 | 58950 |  | 2183.3333
Chiller No 2- |  |  | kwh | 59198.97 | 59199 | 0.03 | -1 |  | -0.037037
Chiller Water pump Panel- 630A |  |  | kwh | 1030659.3 | 1033005 | 2345.7 | 59047 |  | 2186.9259
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 614 |  | 22.7407
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 186.95 |  | 6.9241
Sub Total | [5 empty] | 9521.27 | 294685.21 |  | 10914.267
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 498182.83 | 499028 | 845.17 | 23553 |  | 872.3333
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144640 | 0.13 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606 | -0.07 | -0.07 |  | -0.0025926
Main Lighting and Small power Panel |  |  | kwh | 429772.55 | 430325 | 552.45 | 13515 |  | 500.5556
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 13353 | 13434 | 81 | 5672 |  | 210.0741
Chiller No -3 - 1200A |  |  | kwh | 68110.68 | 68111 | 0.32 | 68111 |  | 2522.6296
Chiller No-4 - 1200A |  |  | Kwh | 591627.75 | 596395 | 4767.25 | 7106.64 |  | 263.2089
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 48968.68 | 49051 | 82.32 | 2334 |  | 86.4444
Sub Total | [5 empty] | 6328.57 | 120291.64 | 922.53 | 4455.2459
|  |  | Total TR1 & TR2 |  |  | 15849.84 | 416560.74 | 383.56 | 15428.1756
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.182 |  | 0.0067407
5th floor spa |  |  | KWh | 2457.1 | 2460 | 2.9 | 101 |  | 3.7407
5th Floor |  |  | KWh | 158972.7 | 159169 | 196.3 | 5870 |  | 217.4074
12th Floor |  |  | KWh | 159915.88 | 160130 | 214.12 | 5531 |  | 204.8519
20th Floor |  |  | KWh | 55424.42 | 55692 | 267.58 | 7121 |  | 263.7407
27th Floor |  |  | KWh | 249886.57 | 250333 | 446.43 | 7159 |  | 265.1481
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 81191.51 | 81292 | 100.49 | 2298 |  | 85.1111
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855782 | 855792 | 10 | 320 |  | 11.8519
Main kitchen power panel no 2 |  |  | KWh | 885932 | 885933 | 1 | 237 |  | 8.7778
Prato kitchen power panel |  |  | KWh | 2553.07 | 2559 | 5.93 | 280 |  | 10.3704
San- Qi Indian Kitchen |  |  | KWh | 12387.5 | 12447 | 59.5 | 1477 |  | 54.7037
San- Qi Japanese Kitchen |  |  | KWh | 7139 | 7193 | 54 | 1476.05 |  | 54.6685
The club kitchen |  |  | KWh | 702629 | 702673 | 44 | 1111 |  | 41.1481
AER Kitchen |  |  | KWh | 672391 | 672455 | 64 | 2430 |  | 90
COLD ROOM'S |  |  | KWh | 830307 | 830419 | 112 | 2688 |  | 99.5556
Ball Room 1 kitchen |  |  | KWh | 525838.04 | 526181 | 342.96 | 6720 |  | 248.8889
Ball Room 2 kitchen |  |  | KWh | 638467.72 | 638548 | 80.28 | 2070 |  | 76.6667
B1 Laundry |  |  | kwh | 108076.42 | 108101 | 24.58 | 489 |  | 18.1111
STP Electrical |  |  | kwh | 19604 | 19771 | 167 | 5000 |  | 185.1852
Cooling Tower |  |  | kwh | 496173 | 496936 | 763 | 16803 |  | 622.3333
Total |  |  |  | 0 | 0 | 1728.25 | 44610 |  | 1652.2222
MOCK Up Room |  |  | Kwh | 460767.32 | 460802 | 34.68 | 34.68 |  | 1.2844
27th Floor |  |  | Kwh | 81289.5 | 81307 | 17.5 | 17.5 |  | 0.64815
Physic57 |  |  | Kwh | 152878.01 | 152900 | 21.99 | 21.99 |  | 0.81444
Pinoor Legal- Lighting |  |  | Kwh | 65120.4 | 65131 | 10.6 | 10.6 |  | 0.39259
Pinoor Legal- Lighting |  |  | Kwh | 3273.6 | 3274 | 0.4 | 0.4 |  | 0.014815
20th Floor Project office |  |  |  | 28000.92 | 28005 | 4.08 | 4.08
WATER
R.o.plant |  |  | KL | 245276 | 245311 | 35 | 887 |  | 32.8519
STP Water Prod |  |  | KL | 185696 | 185782 | 86 | 2251 |  | 83.3704
Total water Produce |  |  |  | 0 |  | 121 | 2991 |  | 110.7778
Domestic Zone-1 |  |  | KL | 414045 | 414094 | 49 | 1208 |  | 44.7407
Domestic Zone-2 |  |  | KL | 102596 | 102607 | 11 | 264 |  | 9.7778
Domestic Zone-3 |  |  | KL | 97827 | 97844 | 17 | 417 |  | 15.4444
Flush Zone -1 |  |  | KL | 149830 | 149838 | 8 | 305 |  | 11.2963
Flush Zone -2 |  |  | KL | 7338 | 7345 | 7 | 160 |  | 5.9259
Flush Zone -3 |  |  | KL | 5347 | 5354 | 7 | 216 |  | 8
Total water consum | [5 empty] | 99 | 2570 |  | 95.1852
Water Branches
Branches
Swimming pool |  |  | KL | 7484 | 7484 | 0 | 57 |  | 2.1111
B2 Laundry |  |  | KL | 35924 | 35924 | 0 | 50 |  | 1.8519
Boiler Feed Water |  |  | KL | 19692 | 19694 | 2 | 126 |  | 4.6667
Total |  |  |  | 0 |  | 2 | 191 |  | 7.0741
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62518 | 62589 | 71 | 152 |  | 5.6296
STP flush(new water meter) |  |  | KL | 32542 | 32542 | 0 | 12 |  | 0.44444
Garden Water Pump |  |  | KL | 4543 | 4559 | 16 | 271 |  | 10.037
Total |  |  |  | 0 |  | 87 | 802 |  | 29.7037
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11457 | 11467 | 10 | 10 |  | 0.37037
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8279 | 8285 | 6 | 58 |  | 2.1481
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 3.5185
Total | [5 empty] | 16 | 88 |  | 3.2593
Total Domestic Water (R.O +BMC) |  |  | KL |  |  | 96 | 108 |  | 4
Total Domestic Consumption |  |  | KL |  |  | 91 | 96 |  | 3.5556
Total STP Consumption |  |  | KL |  |  | 87 | 93 |  | 3.4444
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 831372.91 | 831578 | 205.09 | 5489.54 | 41.018 | 203.3163
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 146182.97 | 146236 | 53.03 | 1548.56 |  | 57.3541
Sanqi IndianGas meter Reading |  |  | m3 | 31404.2 | 31404.2 | 0 | 0.2 |  | 0.0074074
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970.6 | 8970.6 | 0 | 0.9 |  | 0.033333
Boiler Gas Consumption | [5 empty] | 356.88 | 2374.2 |  | 87.9333
Running Hrs
DG Set - 1 |  |  | hr | 0 |  | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 |  | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40059.1 | 40059.1 | 0 | 312.62 |  | 11.5785
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41730.34 | 41730.34 | 0 | 71.95 |  | 2.6648
Chiller - 4 |  |  | hr | 32595 | 32619.04 | 24.04 | 49.11 |  | 1.8189
Steam Boiler -1 |  |  | hr | 22791.36 | 22791.36 | 0 | 51.77 | 24.04 | 1.9174
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.72 | 0 | 8 |  | 0.2963
Steam Boiler -3 |  |  | hr | 70392.18 | 70401.96 | 9.78 | 37.86 | 9.78 | 1.4022
Hot Water Generator -1 |  |  | hr | 1817.18 | 1824.81 | 7.63 | 207.95 |  | 7.7019
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0044444
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4826.95 | 113172 |  | 4191.5556
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 28.78% | 7.1091 |  | 0.2633
Total Chillers Units |  |  | kwh |  |  | 4767.47 | 134166.53 |  | 4969.1307
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 28.42% | 8.4337 |  | 0.31236
Total Lighting Units |  |  | kwh |  |  | 2773.98 | 66534 |  | 2464.2222
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 16.54% | 4.1805 |  | 0.15483
Total power Units |  |  | Kwh |  |  | 1176.54 | 31816 |  | 1178.3704
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.015% | 2.0012 |  | 0.074118
Total mansion power Units |  |  | Kwh |  |  | 845.17 | 26949 |  | 998.1111
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.039% | 1.687 |  | 0.06248
Total fire & em, power Units |  |  | Kwh |  |  | 1296.4 | 33816 |  | 1252.4444
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.729% | 2.1299 |  | 0.078886
Lower Basement |  |  | KWh | 38024.69 | 38104 | 79.31
upper basement |  |  | KWh | 92856.51 | 93230 | 373.49
Level 1 |  |  | KWh | 43914 | 44117 | 203
Level 2 |  |  | KWh | 6525.9 | 6533 | 7.1
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2457.1 | 2460 | 2.9
5th Floor |  |  | KWh | 158972.7 | 159169 | 196.3
12th Floor |  |  | KWh | 159915.88 | 160130 | 214.12
20th Floor |  |  | KWh | 55424.42 | 55692 | 267.58
27th Floor |  |  | KWh | 249886.57 | 250333 | 446.43
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 81191.51 | 81292 | 100.49
1890.72
Note on F55: akash.hebale: meter display faulty

## 28
Daily Utility Consumption Report
Prepaired by----Nilesh | 2021-05-28 | occupancy | 71% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 30 | Last year same month avg
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION | [10 empty] | 1691553
BEST Supply 11KV |  |  | kwh | 275096 | 291944 | 16848 | 446967 | 12000 | 15963.1071
BEST supply |  |  | KVAH | 276912 | 293842 | 16930 | 449601 | 12000 | 16057.1786 | 1375467 | 1703438
Transformer - 1 - 2500KVA |  |  | kwh | 1406705 | 1423014 | 16309 | 432300 | -4057.1786 | 15439.2857
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0 |  | 170
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 16309 | 417779 | 539 | 14920.6786
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1682624 | 1683082 | 458 | 12425 | 800 | 443.75
356.25
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 4 | 40 | 1120 | 65 | 40
BMC |  |  | KL | 139376 | 139436 | 60 | 1624 |  | 58
Total water | [5 empty] | 100 | 2744 | -33 | 98
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 16930 | 9 | 152370 | 4046409 |  | 144514.6071
C.N.G |  |  | Cu.Mtr | 458 | 51.45 | 23564.1 | 628783.729 |  | 22456.5617
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 60 | 134 | 8040 | 217616 |  | 7772
Water Tanker |  |  | KL | 40 | 80 | 3200 | 89600
Total cost | [5 empty] | 187174.1 | 4982408.729 |  | 177943.1689
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 940873 | 943358 | 2485 | 56899 |  | 2032.1071
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 87.75
Fire Emergency Power Panel - 1000A |  |  | kwh | 129041 | 130320 | 1279 | 35095 |  | 1253.3929
Main Power Panel -1600A |  |  | kwh | 151412 | 152607 | 1195 | 33011 |  | 1178.9643
Main Lighting and Small power Panel |  |  | kwh | 299149 | 301259 | 2110 | 54606 |  | 1950.2143
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 889 | 889 | 0 | 888.77 |  | 31.7418
Chiller No 1 |  |  | kwh | 240478 | 240478 | 0 | 58950 |  | 2105.3571
Chiller No 2- |  |  | kwh | 59199 | 59199 | 0 | -1 |  | -0.035714
Chiller Water pump Panel- 630A |  |  | kwh | 1033005 | 1035334 | 2329 | 61376 |  | 2192
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 614 |  | 21.9286
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 186.95 |  | 6.6768
Sub Total | [5 empty] | 9398 | 304083.21 |  | 10860.1146
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 499028 | 499860 | 832 | 24385 |  | 870.8929
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606 | 539606.07 | 0.07 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 430325 | 430926 | 601 | 14116 |  | 504.1429
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 13434 | 13516 | 82 | 5754 |  | 205.5
Chiller No -3 - 1200A |  |  | kwh | 68111 | 68111 | 0 | 68111 |  | 2432.5357
Chiller No-4 - 1200A |  |  | Kwh | 596395 | 601191 | 4796 | 11902.64 |  | 425.0943
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711.33 | 0.33 | 0.33 |  | 0.011786
B2-Loundry power panel |  |  | kwh | 49051 | 49264 | 213 | 2547 |  | 90.9643
Sub Total | [5 empty] | 6524.4 | 126816.04 | 925.6 | 4529.1443
|  |  | Total TR1 & TR2 |  |  | 15922.4 | 432483.14 | 386.6 | 15445.8264
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.182 |  | 0.0065
5th floor spa |  |  | KWh | 2460 | 2464 | 4 | 105 |  | 3.75
5th Floor |  |  | KWh | 159169 | 159360 | 191 | 6061 |  | 216.4643
12th Floor |  |  | KWh | 160130 | 160348 | 218 | 5749 |  | 205.3214
20th Floor |  |  | KWh | 55692 | 55940 | 248 | 7369 |  | 263.1786
27th Floor |  |  | KWh | 250333 | 250705 | 372 | 7531 |  | 268.9643
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 81292 | 81418 | 126 | 2424 |  | 86.5714
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855792 | 855806 | 14 | 334 |  | 11.9286
Main kitchen power panel no 2 |  |  | KWh | 885933 | 885934 | 1 | 238 |  | 8.5
Prato kitchen power panel |  |  | KWh | 2559 | 2566 | 7 | 287 |  | 10.25
San- Qi Indian Kitchen |  |  | KWh | 12447 | 12505 | 58 | 1535 |  | 54.8214
San- Qi Japanese Kitchen |  |  | KWh | 7193 | 7250 | 57 | 1533.05 |  | 54.7518
The club kitchen |  |  | KWh | 702673 | 702712 | 39 | 1150 |  | 41.0714
AER Kitchen |  |  | KWh | 672455 | 672565 | 110 | 2540 |  | 90.7143
COLD ROOM'S |  |  | KWh | 830419 | 830553 | 134 | 2822 |  | 100.7857
Ball Room 1 kitchen |  |  | KWh | 526181 | 526526 | 345 | 7065 |  | 252.3214
Ball Room 2 kitchen |  |  | KWh | 638548 | 638625 | 77 | 2147 |  | 76.6786
B1 Laundry |  |  | kwh | 108101 | 108112 | 11 | 500 |  | 17.8571
STP Electrical |  |  | kwh | 19771 | 19920 | 149 | 5149 |  | 183.8929
Cooling Tower |  |  | kwh | 496936 | 497815 | 879 | 17682 |  | 631.5
Total |  |  |  | 0 |  | 1881 | 46491 |  | 1660.3929
MOCK Up Room |  |  | Kwh | 460802 | 460836 | 34 | 34 |  | 1.2143
27th Floor |  |  | Kwh | 81307 | 81325 | 18 | 18 |  | 0.64286
Physic57 |  |  | Kwh | 152900 | 152923 | 23 | 23 |  | 0.82143
Pinoor Legal- Lighting |  |  | Kwh | 65131 | 65142 | 11 | 11 |  | 0.39286
Pinoor Legal- Lighting |  |  | Kwh | 3274 | 3274 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 28005 | 28010 | 5 | 5
WATER |  |  |  |  | aaaa
R.o.plant |  |  | KL | 245311 | 245339 | 28 | 915 |  | 32.6786
STP Water Prod |  |  | KL | 185782 | 185862 | 80 | 2331 |  | 83.25
Total water Produce |  |  |  | 0 |  | 108 | 3099 |  | 110.6786
Domestic Zone-1 |  |  | KL | 414094 | 414145 | 51 | 1259 |  | 44.9643
Domestic Zone-2 |  |  | KL | 102607 | 102614 | 7 | 271 |  | 9.6786
Domestic Zone-3 |  |  | KL | 97844 | 97862 | 18 | 435 |  | 15.5357
Flush Zone -1 |  |  | KL | 149838 | 149842 | 4 | 309 |  | 11.0357
Flush Zone -2 |  |  | KL | 7345 | 7351 | 6 | 166 |  | 5.9286
Flush Zone -3 |  |  | KL | 5354 | 5360 | 6 | 222 |  | 7.9286
Total water consum | [5 empty] | 92 | 2662 |  | 95.0714
Water Branches
Branches
Swimming pool |  |  | KL | 7484 | 7484 | 0 | 57 |  | 2.0357
B2 Laundry |  |  | KL | 35924 | 35938 | 14 | 64 |  | 2.2857
Boiler Feed Water |  |  | KL | 19694 | 19699 | 5 | 129 |  | 4.6071
Total |  |  |  | 0 |  | 19 | 208 |  | 7.4286
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62589 | 62645 | 56 | 137 |  | 4.8929
STP flush(new water meter) |  |  | KL | 32542 | 32542 | 0 | 12 |  | 0.42857
Garden Water Pump |  |  | KL | 4559 | 4559 | 0 | 255 |  | 9.1071
Total |  |  |  | 0 |  | 56 | 771 |  | 27.5357
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11467 | 11473 | 6 | 6 |  | 0.21429
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8285 | 8289 | 4 | 56 |  | 2
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 3.3929
Total | [5 empty] | 10 | 82 |  | 2.9286
Total Domestic Water (R.O +BMC) |  |  | KL |  |  | 88 | 100 |  | 3.5714
Total Domestic Consumption |  |  | KL |  |  | 88 | 93 |  | 3.3214
Total STP Consumption |  |  | KL |  |  | 56 | 62 |  | 2.2143
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 831578 | 831775 | 197 | 5686.54 |  | 203.0907
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0
BallRoom Gas |  |  | m3 | 146236 | 146302 | 66 | 1614.56 |  | 57.6629
Sanqi IndianGas meter Reading |  |  | m3 | 31404.2 | 31404 | -0.2 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8970.6 | 8971 | 0.4 | 1.3 |  | 0.046429
Boiler Gas Consumption | [5 empty] | 194.8
Running Hrs
DG Set - 1 |  |  | hr | 0 |  | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 |  | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40059.1 | 40059 | -0.1 | 312.52 |  | 11.1614
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | -0.1 | 0
Chiller - 3 |  |  | hr | 41730.34 | 41730 | -0.34 | 71.61 |  | 2.5575 |  |  | -15
Chiller - 4 |  |  | hr | 32619.04 | 32643.16 | 24.12 | 73.23 |  | 2.6154
Steam Boiler -1 |  |  | hr | 22791.36 | 22799 | 7.64 | 59.41 | 31.42 | 2.1218
Steam Boiler -2 |  |  | hr | 25051.72 | 25051.82 | 0.1 | 8.1 |  | 0.28929
Steam Boiler -3 |  |  | hr | 70401.96 | 70402 | 0.04 | 37.9 | 0.14 | 1.3536
Hot Water Generator -1 |  |  | hr | 1824.81 | 1832 | 7.19 | 215.14 |  | 7.6836
Hot Water Generator -2 |  |  | hr | 4636.88 | 4636.88 | 0 | -0.12 |  | -0.0042857
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4814.33 | 117986.33 |  | 4213.7975
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 28.58% | 7.3948 |  | 0.2641
Total Chillers Units |  |  | kwh |  |  | 4796 | 138962.53 |  | 4962.9475
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 28.47% | 8.7183 |  | 0.31137
Total Lighting Units |  |  | kwh |  |  | 2711 | 69245 |  | 2473.0357
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 16.09% | 4.3414 |  | 0.15505
Total power Units |  |  | Kwh |  |  | 1195.07 | 33011.07 |  | 1178.9668
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.093% | 2.0721 |  | 0.074005
Total mansion power Units |  |  | Kwh |  |  | 832 | 27781 |  | 992.1786
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 4.938% | 1.7363 |  | 0.062012
Total fire & em, power Units |  |  | Kwh |  |  | 1279 | 35095 |  | 1253.3929
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.591% | 2.2058 |  | 0.07878
Lower Basement |  |  | KWh | 38104 | 38185 | 81
upper basement |  |  | KWh | 93230 | 93616 | 386
Level 1 |  |  | KWh | 44117 | 44322 | 205
Level 2 |  |  | KWh | 6533 | 6542 | 9
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2460 | 2464 | 4
5th Floor |  |  | KWh | 159169 | 159360 | 191
12th Floor |  |  | KWh | 160130 | 160348 | 218
20th Floor |  |  | KWh | 55692 | 55940 | 248
27th Floor |  |  | KWh | 250333 | 250705 | 372
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 81292 | 81418 | 126
1840

## 29
Daily Utility Consumption Report
Prepaired by- Nilesh | 2021-05-29 | occupancy | 98% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 30 | Last year same month avg
|  | humidity | 78%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 291944 | 308857 | 16913 | 463880 | 12000 | 15995.8621 | 1703438 | 1715917
BEST supply |  |  | KVAH | 293842 | 310826 | 16984 | 466585 |  | 16089.1379 | 1375467
Transformer - 1 - 2500KVA |  |  | kwh | 1423014 | 1439384 | 16370 | 448670 | -3995.8621 | 15471.3793
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0 |  |  |  |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0
SubTotal | [5 empty] | 16370 | 434149 | 543 | 14970.6552
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1683082 | 1683400 | 318 | 12743 | 800 | 439.4138
360.5862
WATER CONSUMPTION
Tankers |  |  | KL | 4 | 6 | 60 | 1180 | 65 | 40.6897
BMC |  |  | KL | 139436 | 139493 | 57 | 1681 |  | 57.9655
Total water | [5 empty] | 117 | 2861 | -33.6552 | 98.6552
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | KVAH | 16984 | 9 | 152856 | 4199265 |  | 144802.2414
C.N.G |  |  | Cu.Mtr | 318 | 51.45 | 16361.1 | 645144.829 |  | 22246.3734
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 57 | 134 | 7638 | 225254 |  | 7767.3793
Water Tanker |  |  | KL | 60 | 80 | 4800 | 94400
Total cost | [5 empty] | 181655.1 | 5164063.829 |  | 178071.1665
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 943358 | 945766 | 2408 | 59307 |  | 2045.069
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 2457 |  | 84.7241
Fire Emergency Power Panel - 1000A |  |  | kwh | 130320 | 131674 | 1354 | 36449 |  | 1256.8621
Main Power Panel -1600A |  |  | kwh | 152607 | 153825 | 1218 | 34229 |  | 1180.3103
Main Lighting and Small power Panel |  |  | kwh | 301259 | 303589 | 2330 | 56936 |  | 1963.3103
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 889 | 889 | 0 | 888.77 |  | 30.6472
Chiller No 1 |  |  | kwh | 240478 | 240478 | 0 | 58950 |  | 2032.7586
Chiller No 2- |  |  | kwh | 59199 | 59199 | 0 | -1 |  | -0.034483
Chiller Water pump Panel- 630A |  |  | kwh | 1035334 | 1037660 | 2326 | 63702 |  | 2196.6207
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 614 |  | 21.1724
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 186.95 |  | 6.4466
Sub Total | [5 empty] | 9636 | 313719.21 |  | 10817.9038
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A | GLR |  | kwh | 499860 | 500726 | 866 | 25251 |  | 870.7241
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144639.87 | -0.13 | -0.13 |  | -0.0044828
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606.07 | 0 | 0 |  | 0
Main Lighting and Small power Panel |  |  | kwh | 430926 | 431514 | 588 | 14704 |  | 507.0345
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 13516 | 13596 | 80 | 5834 |  | 201.1724
Chiller No -3 - 1200A |  |  | kwh | 68111 | 68111 | 0 | 68111 |  | 2348.6552
Chiller No-4 - 1200A |  |  | Kwh | 601191 | 606023 | 4832 | 16734.64 |  | 577.0566
Chiller Water pump Panel- 630A |  |  | kwh | 7711.33 | 7711 | -0.33 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 49264 | 49264 | 0 | 2547 |  | 87.8276
1 | [5 empty] | 6365.54 | 133181.58 | 911.46 | 4592.4683 |  |  |  | 776
|  |  | Total TR1 & TR2 |  |  | 16001.54 | 448484.68 | 368.46 | 15464.989
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.182 |  | 0.0062759
5th floor spa |  |  | KWh | 2464 | 2468 | 4 | 109 |  | 3.7586
5th Floor |  |  | KWh | 159360 | 159553 | 193 | 6254 |  | 215.6552
12th Floor |  |  | KWh | 160348 | 160561 | 213 | 5962 |  | 205.5862
20th Floor |  |  | KWh | 55940 | 56221 | 281 | 7650 |  | 263.7931
27th Floor |  |  | KWh | 250705 | 251244 | 539 | 8070 |  | 278.2759
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 81418 | 81507 | 89 | 2513 |  | 86.6552
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855806 | 855817 | 11 | 345 |  | 11.8966
Main kitchen power panel no 2 |  |  | KWh | 885934 | 885935 | 1 | 239 |  | 8.2414
Prato kitchen power panel |  |  | KWh | 2566 | 2573 | 7 | 294 |  | 10.1379
San- Qi Indian Kitchen |  |  | KWh | 12505 | 12561 | 56 | 1591 |  | 54.8621
San- Qi Japanese Kitchen |  |  | KWh | 7250 | 7308 | 58 | 1591.05 |  | 54.8638
The club kitchen |  |  | KWh | 702712 | 702750 | 38 | 1188 |  | 40.9655
AER Kitchen |  |  | KWh | 672565 | 672760 | 195 | 2735 |  | 94.3103
COLD ROOM'S |  |  | KWh | 830553 | 830691 | 138 | 2960 |  | 102.069
Ball Room 1 kitchen |  |  | KWh | 526526 | 526918 | 392 | 7457 |  | 257.1379
Ball Room 2 kitchen |  |  | KWh | 638625 | 638711 | 86 | 2233 |  | 77
B1 Laundry |  |  | kwh | 108112 | 108123 | 11 | 511 |  | 17.6207
STP Electrical |  |  | kwh | 19920 | 20089 | 169 | 5318 |  | 183.3793
Cooling Tower |  |  | kwh | 497815 | 498687 | 872 | 18554 |  | 639.7931
Total |  |  |  | 0 |  | 2034 | 48525 |  | 1673.2759
MOCK Up Room |  |  | Kwh | 460836 | 460871 | 35 | 35 |  | 1.2069
27th Floor |  |  | Kwh | 81325 | 81340 | 15 | 15 |  | 0.51724
Physic57 |  |  | Kwh | 152923 | 152946 | 23 | 23 |  | 0.7931 |  |  | 481
Pinoor Legal- Lighting |  |  | Kwh | 65142 | 65153 | 11 | 11 |  | 0.37931
Pinoor Legal- Lighting |  |  | Kwh | 3274 | 3274 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 28010 | 28014 | 4 | 4
WATER
R.o.plant |  |  | KL | 245339 | 245378 | 39 | 954 |  | 32.8966
STP Water Prod |  |  | KL | 185862 | 185930 | 68 | 2399 |  | 82.7241
Total water Produce |  |  |  |  | 3 | 107 | 3206 |  | 110.5517
Domestic Zone-1 |  |  | KL | 414145 | 414191 | 46 | 1305 |  | 45
Domestic Zone-2 |  |  | KL | 102614 | 102623 | 9 | 280 |  | 9.6552
Domestic Zone-3 |  |  | KL | 97862 | 97897 | 35 | 470 |  | 16.2069
Flush Zone -1 |  |  | KL | 149842 | 149846 | 4 | 313 |  | 10.7931
Flush Zone -2 |  |  | KL | 7351 | 7356 | 5 | 171 |  | 5.8966
Flush Zone -3 |  |  | KL | 5360 | 5372 | 12 | 234 |  | 8.069
Total water consum | [5 empty] | 111 | 2773 |  | 95.6207
Water Branches
Branches
Swimming pool |  |  | KL | 7484 | 7484 | 0 | 57 |  | 1.9655
B2 Laundry |  |  | KL | 35938 | 35938 | 0 | 50 |  | 1.7241
Boiler Feed Water |  |  | KL | 19699 | 19699 | 0 | 124 |  | 4.2759
Total |  |  |  | 0 |  | 0 | 189 |  | 6.5172
Branches ( STP Water ) |  |  | KL | 0
cooling tower filling water |  |  | KL | 62645 | 62711 | 66 | 147 |  | 5.069
STP flush(new water meter) |  |  | KL | 32542 | 32560 | 18 | 30 |  | 1.0345
Garden Water Pump |  |  | KL | 4559 | 4576 | 17 | 272 |  | 9.3793
Total |  |  |  | 0 |  | 101 | 816 |  | 28.1379
Flushing Water |  |  |  | 0 |  |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11473 | 11480 | 7 | 7 |  | 0.24138
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8289 | 8295 | 6 | 58 |  | 2
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 3.2759
Total | [5 empty] | 13 | 85 |  | 2.931
Total Domestic Water (R.O +BMC) |  |  | KL |  |  | 96 | 108 |  | 3.7241
Total Domestic Consumption |  |  | KL |  |  | 107 | 112 |  | 3.8621
Total STP Consumption |  |  | KL |  |  | 101 | 107 |  | 3.6897
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 831775 | 831972 | 197 | 5883.54 |  | 202.8807
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583 | -0.4 | -0.4 |  | -0.013793
BallRoom Gas |  |  | m3 | 146302 | 146368 | 66 | 1680.56 |  | 57.9503
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.044828
Boiler Gas Consumption | [5 empty] | 55.4
Running Hrs
DG Set - 1 |  |  | hr | 0 |  | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 |  | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40059 | 40059 | 0 | 312.52 |  | 10.7766
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41730 | 41730 | 0 | 71.61 |  | 2.4693
Chiller - 4 |  |  | hr | 32643.16 | 32667.24 | 24.08 | 97.31 |  | 3.3555
Steam Boiler -1 |  |  | hr | 22799 | 22799 | 0 | 59.41 | 24.08 | 2.0486
Steam Boiler -2 |  |  | hr | 25051.82 | 25052 | 0.18 | 8.28 |  | 0.28552
Steam Boiler -3 |  |  | hr | 70402 | 70402 | 0 | 37.9 | 0.18 | 1.3069
Hot Water Generator -1 |  |  | hr | 1832 | 1839.44 | 7.44 | 222.58 |  | 7.6752
Hot Water Generator -2 |  |  | hr | 4636.88 | 4637 | 0.12 | 0 |  | 0
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4733.67 | 122720 |  | 4231.7241
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 27.99% | 7.6747 |  | 0.26465
Total Chillers Units |  |  | kwh |  |  | 4832 | 143794.53 |  | 4958.4321
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 28.57% | 9.004 |  | 0.31048
Total Lighting Units |  |  | kwh |  |  | 2918 | 72163 |  | 2488.3793
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 17.25% | 4.5139 |  | 0.15565
Total power Units |  |  | Kwh |  |  | 1218 | 34229.07 |  | 1180.3128
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.202% | 2.1441 |  | 0.073936
Total mansion power Units |  |  | Kwh |  |  | 866 | 28647 |  | 987.8276
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.12% | 1.7875 |  | 0.061639
Total fire & em, power Units |  |  | Kwh |  |  | 1353.87 | 36448.87 |  | 1256.8576
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 8.005% | 2.2859 |  | 0.078824
Lower Basement |  |  | KWh | 38185 | 38267 | 82
upper basement |  |  | KWh | 93616 | 94011 | 395
Level 1 |  |  | KWh | 44322 | 44527 | 205
Level 2 |  |  | KWh | 6542 | 6549 | 7
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2464 | 2468 | 4
5th Floor |  |  | KWh | 159360 | 159553 | 193
12th Floor |  |  | KWh | 160348 | 160561 | 213
20th Floor |  |  | KWh | 55940 | 56221 | 281
27th Floor |  |  | KWh | 250705 | 251244 | 539
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 81418 | 81507 | 89
2008

## 30
Daily Utility Consumption Report
Prepaired by--- Nilesh | 2020-05-30 | occupancy | 62% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 29 | Last year same month avg
|  | humidity | 80%
Description |  |  | Unit | Yesterday |  | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 308857 | 326729 | 17872 | 481752 | 12000 | 16058.4 | 1375467 |  |  | -5400704
BEST supply |  |  | KVAH | 310826 | 328766 | 17940 | 484525 |  | 16150.8333 | 1715917 | 1728480 | 12563 | -5432478
Transformer - 1 - 2500KVA |  |  | kwh | 1439384 | 1456691 | 17307 | 465977 | -4058.4 | 15532.5667 | 1715817 |  |  | 465977
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0 |  |  |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0 |  |  |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0 |  |  |  | 0
SubTotal | [5 empty] | 17307 | 451456 | 565 | 15048.5333 |  |  |  | 0
GAS CONSUMPTION | [12 empty] | 0
Gas consumption |  |  | m3 | 1683400 | 1683884 | 484 | 13227 | 800 | 440.9 |  |  |  | 13227
[8 empty] | 359.1 |  |  |  |  | 0
WATER CONSUMPTION | [12 empty] | 0
Tankers |  |  | KL | 6 | 8 | 80 | 1260 | 65 | 42 |  |  |  | 2
BMC |  |  | KL | 139493 | 139551 | 58 | 1739 |  | 57.9667 |  |  |  | 1739
Total water | [5 empty] | 138 | 2999 | -34.9667 | 99.9667 |  |  |  | 0
DIESEL CONSUMPTION | [12 empty] | 0
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0 |  |  |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0 |  |  |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0 |  |  |  | 0
TOTAL CONSUMPTION UNIT &COST | [12 empty] | 0
Utilities |  |  | Units | [9 empty] | 0
Electricity |  |  | KVAH | 17940 | 9 | 161460 | 4360725 |  | 145357.5
C.N.G |  |  | Cu.Mtr | 484 | 51.45 | 24901.8 | 670046.629 |  | 22334.8876
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0
Water BMC |  |  | Kl | 58 | 134 | 7772 | 233026 |  | 7767.5333
Water Tanker |  |  | KL | 80 | 80 | 6400 | 100800 |  | 3360
Total cost | [5 empty] | 200533.8 | 5364597.629 |  | 178819.921
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 945766 | 948143 | 2377 | 61684 |  | 2056.1333 |  |  |  | 61684
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 347065 | 0 | 0 |  | 0 |  |  |  | 2457
Fire Emergency Power Panel - 1000A |  |  | kwh | 131674 | 132976 | 1302 | 37751 |  | 1258.3667 |  |  |  | 37751
Main Power Panel -1600A |  |  | kwh | 153825 | 155156 | 1331 | 35560 |  | 1185.3333
Main Lighting and Small power Panel |  |  | kwh | 303589 | 305998 | 2409 | 59345 |  | 1978.1667 |  |  |  | 59345
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 889 | 889 | 0 | 888.77 |  | 29.6257 |  |  |  | 888.77
Chiller No 1 |  |  | kwh | 240478 | 240478 | 0 | 58950 |  | 1965 |  |  |  | 58950
Chiller No 2- |  |  | kwh | 59199 | 59199 | 0 | -1 |  | -0.033333 |  |  |  | -1
Chiller Water pump Panel- 630A |  |  | kwh | 1037660 | 1039967 | 2307 | 66009 |  | 2200.3 |  |  |  | 66009
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 614 |  | 20.4667 |  |  |  | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 186.95 |  | 6.2317 |  |  |  | 0
Sub Total | [5 empty] | 9726 | 323445.21 |  | 10781.507 |  |  |  | 0
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732.13 | 0 | 0 |  | 0
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 500726 | 501652 | 926 | 26177 |  | 872.5667
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 144640 | 0.13 | 0 |  | 0
Main Power Panel -1800A |  |  | kwh | 539606.07 | 539606 | -0.07 | -0.07 |  | -0.0023333
Main Lighting and Small power Panel |  |  | kwh | 431514 | 432059 | 545 | 15249 |  | 508.3
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 13596 | 13678 | 82 | 5916 |  | 197.2
Chiller No -3 - 1200A |  |  | kwh | 68111 | 68111 | 0 | 68111 |  | 2270.3667
Chiller No-4 - 1200A |  |  | Kwh | 606023 | 611596 | 5573 | 22307.64 |  | 743.588
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0
B2-Loundry power panel |  |  | kwh | 49264 | 49355 | 91 | 2638 |  | 87.9333
Sub Total | [5 empty] | 7217.06 | 140398.64 | 928.94 | 4679.9547
|  |  | Total TR1 & TR2 |  |  | 16943.06 | 465427.74 | 363.94 | 15514.258
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.182 |  | 0.0060667
5th floor spa |  |  | KWh | 2468 | 2472 | 4 | 113 |  | 3.7667
5th Floor |  |  | KWh | 159553 | 159745 | 192 | 6446 |  | 214.8667
12th Floor |  |  | KWh | 160561 | 160777 | 216 | 6178 |  | 205.9333
20th Floor |  |  | KWh | 56221 | 56522 | 301 | 7951 |  | 265.0333
27th Floor |  |  | KWh | 251244 | 251770 | 526 | 8596 |  | 286.5333
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0
Sanqi |  |  | KWh | 81507 | 81645 | 138 | 2651 |  | 88.3667
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855817 | 855831 | 14 | 359 |  | 11.9667
Main kitchen power panel no 2 |  |  | KWh | 885935 | 885936 | 1 | 240 |  | 8
Prato kitchen power panel |  |  | KWh | 2573 | 2579 | 6 | 300 |  | 10
San- Qi Indian Kitchen |  |  | KWh | 12561 | 12615 | 54 | 1645 |  | 54.8333
San- Qi Japanese Kitchen |  |  | KWh | 7308 | 7363 | 55 | 1646.05 |  | 54.8683
The club kitchen |  |  | KWh | 702750 | 702791 | 41 | 1229 |  | 40.9667
AER Kitchen |  |  | KWh | 672760 | 672954 | 194 | 2929 |  | 97.6333
COLD ROOM'S |  |  | KWh | 830691 | 830852 | 161 | 3121 |  | 104.0333
Ball Room 1 kitchen |  |  | KWh | 526918 | 527299 | 381 | 7838 |  | 261.2667
Ball Room 2 kitchen |  |  | KWh | 638711 | 638809 | 98 | 2331 |  | 77.7
B1 Laundry |  |  | kwh | 108123 | 108146 | 23 | 534 |  | 17.8
STP Electrical |  |  | kwh | 20089 | 20313 | 224 | 5542 |  | 184.7333
Cooling Tower |  |  | kwh | 498687 | 499489 | 802 | 19356 |  | 645.2
Total |  |  |  | 0 |  | 2054 | 50579 |  | 1685.9667
MOCK Up Room |  |  | Kwh | 460871 | 460907 | 36 | 71 |  | 2.3667
27th Floor |  |  | Kwh | 81340 | 81352 | 12 | 27 |  | 0.9
Physic57 |  |  | Kwh | 152946 | 152970 | 24 | 47 |  | 1.5667
Pinoor Legal- Lighting |  |  | Kwh | 65153 | 65164 | 11 | 22 |  | 0.73333
Pinoor Legal- Lighting |  |  | Kwh | 3274 | 3274 | 0 | 0 |  | 0
20th Floor Project office |  |  |  | 28014 | 28016 | 2
WATER
R.o.plant |  |  | KL | 245378 | 245378 | 0 | 954 |  | 31.8
STP Water Prod |  |  | KL | 185930 | 186042 | 112 | 2511 |  | 83.7
Total water Produce | [5 empty] | 112 | 3318 |  | 110.6
Domestic Zone-1 |  |  | KL | 414191 | 414229 | 38 | 1343 |  | 44.7667
Domestic Zone-2 |  |  | KL | 102623 | 102636 | 13 | 293 |  | 9.7667
Domestic Zone-3 |  |  | KL | 97897 | 97931 | 34 | 504 |  | 16.8
Flush Zone -1 |  |  | KL | 149846 | 149848 | 2 | 315 |  | 10.5
Flush Zone -2 |  |  | KL | 7356 | 7363 | 7 | 178 |  | 5.9333
Flush Zone -3 |  |  | KL | 5372 | 5383 | 11 | 245 |  | 8.1667
Total water consum | [5 empty] | 105 | 2878 |  | 95.9333
Water Branches
Branches
Swimming pool |  |  | KL | 7484 | 7484 | 0 | 57 |  | 1.9
B2 Laundry |  |  | KL | 35938 | 35938 | 0 | 50 |  | 1.6667
Boiler Feed Water |  |  | KL | 19699 | 19702 | 3 | 127 |  | 4.2333
Total | [5 empty] | 3 | 192 |  | 6.4
Branches ( STP Water ) |  |  | KL
cooling tower filling water |  |  | KL | 62711 | 62770 | 59 | 206 |  | 6.8667
STP flush(new water meter) |  |  | KL | 32560 | 32578 | 18 | 48 |  | 1.6
Garden Water Pump |  |  | KL | 4576 | 4576 | 0 | 272 |  | 9.0667
Total | [5 empty] | 77 | 893 |  | 29.7667
Flushing Water | [8 empty] | 0
Flush Zone 2 pump meter |  |  | KL | 11480 | 11489 | 9 | 16 |  | 0.53333
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8295 | 8306 | 11 | 69 |  | 2.3
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 3.1667
Total | [5 empty] | 20 | 105 |  | 3.5
Total Domestic Water (R.O +BMC) |  |  | KL |  |  | 58 | 166 |  | 5.5333
Total Domestic Consumption |  |  | KL |  |  | 103 | 215 |  | 7.1667
Total STP Consumption |  |  | KL |  |  | 77 | 184 |  | 6.1333
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 831972 | 832189 | 217 | 6100.54 |  | 203.3513
Prato Kitchen Gas meter Reading |  |  | m3 | 73583 | 73583.4 | 0.4 | 0 |  | 0
BallRoom Gas |  |  | m3 | 146368 | 146433 | 65 | 1745.56 |  | 58.1853
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31404 | 0 | 0 |  | 0
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8971 | 0 | 1.3 |  | 0.043333
Boiler Gas Consumption | [5 empty] | 201.6
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40059 | 40059 | 0 | 312.52 |  | 10.4173
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41730 | 41730 | 0 | 71.61 |  | 2.387
Chiller - 4 |  |  | hr | 32667.24 | 32691.27 | 24.03 | 121.34 |  | 4.0447
Steam Boiler -1 |  |  | hr | 22799 | 22799 | 0 | 59.41 | 24.03 | 1.9803
Steam Boiler -2 |  |  | hr | 25052 | 25051.82 | -0.18 | 8.1 |  | 0.27
Steam Boiler -3 |  |  | hr | 70402 | 70411.74 | 9.74 | 47.64 | 9.56 | 1.588
Hot Water Generator -1 |  |  | hr | 1839.44 | 1847.53 | 8.09 | 230.67 |  | 7.689
Hot Water Generator -2 |  |  | hr | 4637 | 4637 | 0 | 0 |  | 0
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4684 | 127404 |  | 4246.8
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 26.21% | 7.9368 |  | 0.26456
Total Chillers Units |  |  | kwh |  |  | 5573 | 149367.53 |  | 4978.9177
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 31.18% | 9.3159 |  | 0.31053
Total Lighting Units |  |  | kwh |  |  | 2954 | 75117 |  | 2503.9
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 16.53% | 4.6792 |  | 0.15597
Total power Units |  |  | Kwh |  |  | 1330.93 | 35560 |  | 1185.3333
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.447% | 2.2186 |  | 0.073954
Total mansion power Units |  |  | Kwh |  |  | 926 | 29573 |  | 985.7667
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.181% | 1.8394 |  | 0.061312
Total fire & em, power Units |  |  | Kwh |  |  | 1302.13 | 37751 |  | 1258.3667
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.286% | 2.3588 |  | 0.078625
Lower Basement |  |  | KWh | 38267 | 38350 | 83
upper basement |  |  | KWh | 94011 | 94392 | 381
Level 1 |  |  | KWh | 44527 | 44727 | 200
Level 2 |  |  | KWh | 6549 | 6554 | 5
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2468 | 2472 | 4
5th Floor |  |  | KWh | 159553 | 159745 | 192
12th Floor |  |  | KWh | 160561 | 160777 | 216
20th Floor |  |  | KWh | 56221 | 56522 | 301
27th Floor |  |  | KWh | 251244 | 251770 | 526
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 81507 | 81645 | 138
2046

## 31
Daily Utility Consumption Report
Prepaired by--- Devendra | 2021-05-31 | occupancy | 24% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 30 | Last year same month avg
|  | humidity | 80%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 326729 | 344412 | 17683 | 499435 | 12000 | 16110.8065 | 1375467 |  |  | -5383021 | -5383021
BEST supply |  |  | KVAH | 328766 | 346510 | 17744 | 502269 |  | 16202.2258 | 1715917 | 1728480 | 12563 | -5414734
Transformer - 1 - 2500KVA |  |  | kwh | 1456691 | 1473690 | 16999 | 482976 | -4110.8065 | 15579.871 | 1715817 |  |  | 482976
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 2322.58 | 0 | 0 |  | 0 |  |  |  | 0
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 37000 | 0 | 0 |  | 0 |  |  |  | 0
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 40010 | 0 | 0 |  | 0 |  |  |  | 0
SubTotal | [5 empty] | 16999 | 468455 | 684 | 15111.4516 |  |  |  | 0
GAS CONSUMPTION | [12 empty] | 0
Gas consumption |  |  | m3 | 1683884 | 1684524 | 640 | 13867 | 800 | 447.3226 |  |  |  | 13867
[8 empty] | 352.6774 |  |  |  |  | 0
WATER CONSUMPTION | [12 empty] | 0
Tankers |  |  | KL | 8 | 6 | 60 | 1320 | 65 | 42.5806 |  |  |  | 0
BMC |  |  | KL | 139551 | 139612 | 61 | 1800 |  | 58.0645 |  |  |  | 1800
Total water | [5 empty] | 121 | 3120 | -35.6452 | 100.6452 |  |  |  | 0
DIESEL CONSUMPTION | [12 empty] | 0
Boiler House (H.S.D) |  |  | L | 2970 | 2970 | 0 | 0 |  | 0 |  |  |  | 0
D-G Set (H.S.D) |  |  | L | 2000 | 2000 | 0 | 0 |  | 0 |  |  |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4970 | 0 | 0 |  | 0 |  |  |  | 0
TOTAL CONSUMPTION UNIT &COST | [12 empty] | 0
Utilities |  |  | Units | [9 empty] | 0
Electricity |  |  | KVAH | 17744 | 9 | 159696 | 4520421 |  | 145820.0323 |  |  |  | -16044
C.N.G |  |  | Cu.Mtr | 640 | 51.45 | 32928 | 702974.629 |  | 22676.6009 |  |  |  | -282.55
H.S.D |  |  | Ltr | 0 | 69 | 0 | 0 |  | 0 |  |  |  | 69
Water BMC |  |  | Kl | 61 | 134 | 8174 | 241200 |  | 7780.6452 |  |  |  | 78
Water Tanker |  |  | KL | 60 | 80 | 4800 | 105600 |  | 3406.4516 |  |  |  | 0
Total cost | [5 empty] | 205598 | 5570195.629 |  | 179683.73 |  |  |  | 0
BRANCH READINGS & CONSUMPTION | [12 empty] | 0
Transformer No 1 (Sub Feeders) | [12 empty] | 0
Main HVAC Power Panel- 800A |  |  | kwh | 948143 | 950488 | 2345 | 64029 |  | 2065.4516 |  |  |  | 64029
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 0 | 173 | 173 | 173 |  | 5.5806 |  |  |  | -344435
Fire Emergency Power Panel - 1000A |  |  | kwh | 132976 | 134236 | 1260 | 39011 |  | 1258.4194 |  |  |  | 39011
Main Power Panel -1600A |  |  | kwh | 155156 | 156405 | 1249 | 36809 |  | 1187.3871 |  |  |  | 36809
Main Lighting and Small power Panel |  |  | kwh | 305998 | 308173 | 2175 | 61520 |  | 1984.5161 |  |  |  | 61520
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 889 | 889 | 0 | 888.77 |  | 28.67 |  |  |  | 888.77
Chiller No 1 |  |  | kwh | 240478 | 240478 | 0 | 58950 |  | 1901.6129 |  |  |  | 58950
Chiller No 2- |  |  | kwh | 59199 | 59200 | 1 | 0 |  | 0 |  |  |  | -59200
Chiller Water pump Panel- 630A |  |  | kwh | 1039967 | 1042244 | 2277 | 68286 |  | 2202.7742 |  |  |  | -905672
Co-Genrator |  |  | kwh | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0
Lawn Pantry |  |  | kwh | 614 | 614 | 0 | 614 |  | 19.8065 |  |  |  | 0
Pavilion Power |  |  | kwh | 187 | 187 | 0 | 186.95 |  | 6.0306 |  |  |  | -0.05
Sub Total | [5 empty] | 9480 | 332925.21 |  | 10739.5229 |  |  |  | 332925.21
Transformer No 2 (Sub Feeders) | [12 empty] | 0
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 260732 | -0.13 | -0.13 |  | -0.0041935 |  |  |  | -260732.26
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 501652 | 502536 | 884 | 27061 |  | 872.9355 |  |  |  | -447475
Fire Emergency Power Panel - 1000A |  |  | kwh | 144640 | 144640 | 0 | 0 |  | 0 |  |  |  | -144640
Main Power Panel -1800A |  |  | kwh | 539606 | 539606 | 0 | -0.07 |  | -0.0022581 |  |  |  | -539606.07
Main Lighting and Small power Panel |  |  | kwh | 432059 | 432568 | 509 | 15758 |  | 508.3226 |  |  |  | -400553
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 13678 | 13750 | 72 | 5988 |  | 193.1613 |  |  |  | -5390
Chiller No -3 - 1200A |  |  | kwh | 68111 | 68111 | 0 | 68111 |  | 2197.129 |  |  |  | -278815
Chiller No-4 - 1200A |  |  | Kwh | 611596 | 617198 | 5602 | 27909.64 |  | 900.311 |  |  |  | -561378.83
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 7711 | 0 | 0 |  | 0 |  |  |  | -7711
B2-Loundry power panel |  |  | kwh | 49355 | 49625 | 270 | 2908 |  | 93.8065 |  |  |  | -43760 | -2957
Sub Total | [5 empty] | 7336.87 | 147735.51 | 866.13 | 4765.6616 |  |  |  | 147735.51
|  |  | Total TR1 & TR2 |  |  | 16816.87 | 482244.61 | 182.13 | 15556.2777 |  |  |  | 482244.61
Floor lighting & Power consumption | [12 empty] | 0
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0 | 0.182 |  | 0.005871 |  |  |  | -20418.818
5th floor spa |  |  | KWh | 0 | 0 | 0 | 113 |  | 3.6452 |  |  |  | -2246
5th Floor |  |  | KWh | 159745 | 159932 | 187 | 6633 |  | 213.9677 |  |  |  | -146666
12th Floor |  |  | KWh | 160777 | 160998 | 221 | 6399 |  | 206.4194 |  |  |  | -148200
20th Floor |  |  | KWh | 56522 | 56805 | 283 | 8234 |  | 265.6129 |  |  |  | -40337
27th Floor |  |  | KWh | 251770 | 252192 | 422 | 9018 |  | 290.9032 |  |  |  | -234156
34th Floor |  |  | KWh | 85321 | 85321 | 0 | 0 |  | 0 |  |  |  | -85321
Sanqi |  |  | KWh | 81645 | 81749 | 104 | 2755 |  | 88.871 |  |  |  | -76239
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0 | [5 empty] | 0
Kitchen consumption | [12 empty] | 0
Main kitchen power panel no 1 |  |  | KWh | 855831 | 855843 | 12 | 371 |  | 11.9677 |  |  |  | -855090
Main kitchen power panel no 2 |  |  | KWh | 885936 | 885937 | 1 | 241 |  | 7.7742 |  |  |  | -885635
Prato kitchen power panel |  |  | KWh | 2579 | 2586 | 7 | 307 |  | 9.9032 |  |  |  | -1972
San- Qi Indian Kitchen |  |  | KWh | 12615 | 12669 | 54 | 1699 |  | 54.8065 |  |  |  | -9271
San- Qi Japanese Kitchen |  |  | KWh | 7363 | 7419 | 56 | 1702.05 |  | 54.9048 |  |  |  | -4006.95
The club kitchen |  |  | KWh | 702791 | 702839 | 48 | 1277 |  | 41.1935 |  |  |  | -700285
AER Kitchen |  |  | KWh | 672954 | 673032 | 78 | 3007 |  | 97 |  |  |  | -667018
COLD ROOM'S |  |  | KWh | 830852 | 831010 | 158 | 3279 |  | 105.7742 |  |  |  | -823505
Ball Room 1 kitchen |  |  | KWh | 527299 | 527658 | 359 | 8197 |  | 264.4194 |  |  |  | -508541
Ball Room 2 kitchen |  |  | KWh | 638809 | 638898 | 89 | 2420 |  | 78.0645 |  |  |  | -634058
B1 Laundry |  |  | kwh | 108146 | 108158 | 12 | 546 |  | 17.6129 |  |  |  | -107066
STP Electrical |  |  | kwh | 20313 | 20506 | 193 | 5735 |  | 185 |  |  |  | -9036
Cooling Tower |  |  | kwh | 499489 | 500294 | 805 | 20161 |  | 650.3548 |  |  |  | -459972
Total | [5 empty] | 1872 | 52451 |  | 1691.9677 |  |  |  | 52451
MOCK Up Room |  |  | Kwh | 460907 | 460935 | 28 | 99 |  | 3.1935 |  |  |  | -459168
27th Floor |  |  | Kwh | 81352 | 81375 | 23 | 50 |  | 1.6129 |  |  |  | -80869
Physic57 |  |  | Kwh | 152970 | 153064 | 94 | 141 |  | 4.5484 |  |  |  | -151664
Pinoor Legal- Lighting |  |  | Kwh | 65164 | 65174.6 | 10.6 | 32.6 |  | 1.0516 |  |  |  | -64801.4
Pinoor Legal- Lighting |  |  | Kwh | 3274 | 3273.6 | -0.4 | -0.4 |  | -0.012903 |  |  |  | -3272.4
20th Floor Project office |  |  |  | 28016 | 28022 | 6 | 6 |  | 0.19355
WATER | [12 empty] | 0
R.o.plant |  |  | KL | 245378 | 245488 | 110 | 1064 |  | 34.3226 |  |  |  | -243460
STP Water Prod |  |  | KL | 186042 | 186121 | 79 | 2590 |  | 83.5484 |  |  |  | -180941
Total water Produce | [5 empty] | 189 | 3507 |  | 113.129 |  |  |  | 3507
Domestic Zone-1 |  |  | KL | 414229 | 414283 | 54 | 1397 |  | 45.0645 |  |  |  | -411489
Domestic Zone-2 |  |  | KL | 102636 | 102648 | 12 | 305 |  | 9.8387 |  |  |  | -102038
Domestic Zone-3 |  |  | KL | 97931 | 97950 | 19 | 523 |  | 16.871 |  |  |  | -96904
Flush Zone -1 |  |  | KL | 149848 | 149852 | 4 | 319 |  | 10.2903 |  |  |  | -149214
Flush Zone -2 |  |  | KL | 7363 | 7369 | 6 | 184 |  | 5.9355 |  |  |  | -7001
Flush Zone -3 |  |  | KL | 5383 | 5391 | 8 | 253 |  | 8.1613 |  |  |  | -4885
Total water consum | [5 empty] | 103 | 2981 |  | 96.1613 |  |  |  | 2981
Water Branches | [12 empty] | 0
Branches | [12 empty] | 0
Swimming pool |  |  | KL | 7484 | 7484 | 0 | 57 |  | 1.8387 |  |  |  | -7374
B2 Laundry |  |  | KL | 35938 | 35953 | 15 | 65 |  | 2.0968 |  |  |  | -35763
Boiler Feed Water |  |  | KL | 19702 | 19708 | 6 | 133 |  | 4.2903 |  |  |  | -19484
Total | [5 empty] | 21 | 213 |  | 6.871 |  |  |  | 213
Branches ( STP Water ) |  |  | KL |  |  |  | 0 | [5 empty] | 0
cooling tower filling water |  |  | KL | 62770 | 62834 | 64 | 270 |  | 8.7097 |  |  |  | -60904
STP flush(new water meter) |  |  | KL | 32578 | 32578 | 0 | 48 |  | 1.5484 |  |  |  | -32187
Garden Water Pump |  |  | KL | 4576 | 4576 | 0 | 272 |  | 8.7742 |  |  |  | -4096
Total | [5 empty] | 64 | 957 |  | 30.871 |  |  |  | 957
Flushing Water | [6 empty] | 0 |  | 0 |  |  |  | 0
Flush Zone 2 pump meter |  |  | KL | 11489 | 11497 | 8 | 24 |  | 0.77419 |  |  |  | -11235
Flush Zone 3 Pump Meter (wtp transfer ) |  |  | KL | 8306 | 8312 | 6 | 75 |  | 2.4194 |  |  |  | -8051
Flush Tanker |  |  | KL |  |  | 0 | 95 |  | 3.0645 |  |  |  | 95
Total | [5 empty] | 14 | 119 |  | 3.8387 |  |  |  | 119
Total Domestic Water (R.O +BMC) |  |  | KL |  |  | 171 | 337 |  | 10.871 |  |  |  | 337
Total Domestic Consumption |  |  | KL |  |  | 99 | 314 |  | 10.129 |  |  |  | 314
Total STP Consumption |  |  | KL |  |  | 64 | 248 |  | 8 |  |  |  | 248
0
GAS Branch CONSUMPTION | [12 empty] | 0
H.W.G. Gas meter reading |  |  | m3 | 832189 | 832366 | 177 | 6277.54 |  | 202.5013 |  |  |  | -819810.92
Prato Kitchen Gas meter Reading |  |  | m3 | 73583.4 | 73583.4 | 0 | 0 |  | 0 |  |  |  | -73583.4
BallRoom Gas |  |  | m3 | 146433 | 146491 | 58 | 1803.56 |  | 58.1794 |  |  |  | -142883.88
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 31406 | 2 | 2 |  | 0.064516 |  |  |  | -31402
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 8972 | 1 | 2.3 |  | 0.074194 |  |  |  | -8967.4
Boiler Gas Consumption | [5 empty] | 402 | 402 | [5 empty] | 402
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40059 | 40059 | 0 | 312.52 |  | 10.0813
Chiller - 2 |  |  | hr | 300 | 300 | 0 | 0 | 0 | 0
Chiller - 3 |  |  | hr | 41730 | 41730 | 0 | 71.61 |  | 2.31
Chiller - 4 |  |  | hr | 32691.27 | 32715 | 23.73 | 145.07 |  | 4.6797
Steam Boiler -1 |  |  | hr | 22799 | 22807.24 | 8.24 | 67.65 | 31.97 | 2.1823
Steam Boiler -2 |  |  | hr | 25051.82 | 25051.82 | 0 | 8.1 |  | 0.26129
Steam Boiler -3 |  |  | hr | 70411.74 | 70411.74 | 0 | 47.64 | 0 | 1.5368
Hot Water Generator -1 |  |  | hr | 1847.53 | 1854.3 | 6.77 | 237.44 |  | 7.6594
Hot Water Generator -2 |  |  | hr | 4637 | 4637 | 0 | 0 |  | 0
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 4621.87 | 132025.87 |  | 4258.899
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 26.14% | 8.1982 |  | 0.26446
Total Chillers Units |  |  | kwh |  |  | 5603 | 154970.53 |  | 4999.0494
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 31.69% | 9.6327 |  | 0.31073
Total Lighting Units |  |  | kwh |  |  | 2684 | 77801 |  | 2509.7097
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 15.18% | 4.831 |  | 0.15584
Total power Units |  |  | Kwh |  |  | 1249 | 36809 |  | 1187.3871
% of power Units of Total Con.(LT) |  |  | % |  |  | 7.063% | 2.2892 |  | 0.073847
Total mansion power Units |  |  | Kwh |  |  | 1057 | 30630 |  | 988.0645
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 5.977% | 1.8991 |  | 0.061262
Total fire & em, power Units |  |  | Kwh |  |  | 1260 | 39011 |  | 1258.4194
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 7.125% | 2.43 |  | 0.078387
Lower Basement |  |  | KWh | 38350 | 38434 | 84
upper basement |  |  | KWh | 94392 | 94790 | 398
Level 1 |  |  | KWh | 44727 | 44933 | 206
Level 2 |  |  | KWh | 6554 | 6560 | 6
2nd floor plant room |  |  | KWh | 20419 | 20419 | 0
5th floor spa |  |  | KWh | 2472 | 2472 | 0
5th Floor |  |  | KWh | 159745 | 159932 | 187
12th Floor |  |  | KWh | 160777 | 160998 | 221
20th Floor |  |  | KWh | 56522 | 56805 | 283
27th Floor |  |  | KWh | 251770 | 252192 | 422
34th Floor |  |  | KWh | 85321 | 85321 | 0
Sanqi |  |  | KWh | 81645 | 81749 | 104
1911

## Daily HLP (2)
Date | Date | Min.Tem (Degee) | Occu. | Gas |  |  | Boiler Running Hrs |  |  | Total boiler | Hot Water Generator |  |  | Total HWG RH
|  |  | % | Total Units(CuM) | Rate | Total Cost(Rs) | Boiler1 | Boiler2 | Boiler3 |  | HWG1 | HWG2 | HWG3
1 | 1 |  | 5777297 | 12 | 0 | 0 | 0 | 82 | 0 | 82 | 0 | 17 | 0 | 17
2 | 2 |  | 5793328 | 42 | 0 | 0 | 0 | 93 | 0 | 93 | 0 | 15 | 0 | 15
3 | 3 |  | 5825643 | 61 | 0 | 0 | 0 | 78 | 0 | 78 | 0 | 17 | 0 | 17
4 | 4 |  | 5809417 | 62 | 0 | 0 | 0 | 85 | 0 | 85 | 0 | 15 | 0 | 15
5 | 5 |  | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | #REF!
6 | 6 |  | 5857109 | 39 | 0 | 0 | 0 | 41 | 0 | 41 | 0 | 31 | 0 | 31
7 | 7 |  | 5872131 | 31 | 0 | 0 | 0 | 34 | 0 | 34 | 0 | 2 | 0 | 2
8 | 8 |  | 5891695 | 78 | 0 | 0 | 0 | 141.4 | 0 | 141.4 | 0 | 15 | 0 | 15
9 | 9 |  | 5907092 | 40 | 0 | 0 | 0 | 112.6 | 0 | 112.6 | 0 | 16 | 0 | 16
10 | 10 |  | 5922347 | 24 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 17 | 0 | 17
11 | 11 |  | 19957.82 | 26 | 0 | 0 | 0 | 39.61 | 0 | 39.61 | 0 | 14 | 0 | 14
12 | 12 |  | 35217.71 | 35 | 0 | 0 | 0 | 43.21 | 0 | 43.21 | 0 | 9 | 0 | 9
13 | 13 |  | 49888.73 | 52 | 0 | 0 | 0 | 43.45 | 0 | 43.45 | 0 | 11 | 0 | 11
14 | 14 |  | 64319.28 | 46 | 0 | 0 | 0 | 42.8 | 0 | 42.8 | 10 | 1 | 0 | 11
15 | 15 |  | 81436 | 42 | 0 | 0 | 0 | 89.93 | 0 | 89.93 | 10 | 1 | 0 | 11

## Sheet1
Daily Utility Consumption Report
Date :- | 2015-11-20 | Prepaired by- Robert |  | Occupancy% | Electricity | Water | Gas
Last year same month(LYSM) |  |  |  | Last year same month avg | 0 | 0 | 0 | Ambient Temp | HUMIDITY%
HTP MD-1699 | H.T P.F--0.999 | occupancy | 80% |  |  |  |  | 31 | 82
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh
Transformer - 1 - 2500KVA |  |  | kwh
Transformer - 2 -2500KVA |  |  | kwh
DG set- 1 - 1425KVA |  |  | kwh
DG set- 2 - 1425KVA |  |  | kwh
SubTotal
GAS CONSUMPTION
Gas consumption |  |  | m3
WATER CONSUMPTION
Tankers |  |  | KL
BMC |  |  | KL
Total water
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L
D-G Set (H.S.D) |  |  | L
Total HSD (H.S.D.) Stock |  |  | L
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units
Electricity |  |  | kwh
C.N.G |  |  | Cu.Mtr
H.S.D |  |  | Ltr
Water |  |  | Kl
Total cost
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh
Fire Emergency Power Panel - 1000A |  |  | kwh
Main Power Panel -1600A |  |  | kwh
Main Lighting and Small power Panel |  |  | kwh
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh
Chiller No 1 |  |  | kwh
Chiller No 2- |  |  | kwh
Chiller Water pump Panel- 630A |  |  | kwh
Co-Genrator |  |  | kwh
Lawn Pantry |  |  | kwh
Pavilion Power |  |  | kwh
Sub Total
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh
Fire Emergency Power Panel - 1000A |  |  | kwh
Main Power Panel -1800A |  |  | kwh
Main Lighting and Small power Panel |  |  | kwh
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh
Chiller No -3 - 1200A |  |  | kwh
Chiller No-4 - 1200A |  |  | Kwh
Chiller Water pump Panel- 630A |  |  | kwh
B2-Loundry power panel |  |  | kwh
Sub Total
Total TR1 & TR2
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh
5th floor spa |  |  | KWh
5th Floor |  |  | KWh
12th Floor |  |  | KWh
20th Floor |  |  | KWh
27th Floor |  |  | KWh
34th Floor |  |  | KWh
Sanqi |  |  | KWh
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh
Main kitchen power panel no 2 |  |  | KWh
Prato kitchen power panel |  |  | KWh
San- Qi Indian Kitchen |  |  | KWh
San- Qi Japanese Kitchen |  |  | KWh
The club kitchen |  |  | KWh
COLD ROOM'S |  |  | KWh
Ball Room 1 kitchen |  |  | KWh
Ball Room 2 kitchen |  |  | KWh
B1 Laundry |  |  | kwh
STP Electrical |  |  | kwh
ETP electrical |  |  | kwh
Total
WATER
STP Water Prod |  |  | KL
Domestic Zone-1 |  |  | KL
Domestic Zone-2 |  |  | KL
Domestic Zone-3 |  |  | KL
Flush Zone -1 |  |  | KL
Flush Zone -2 |  |  | KL
Flush Zone -3 |  |  | KL
Swimming pool |  |  | KL
B2 Laundry |  |  | KL
Boiler Feed Water |  |  | KL
R.o.plant |  |  | KL
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3
BallRoom Gas |  |  | m3
Percentag of ele, unit per area
Total HVAC units |  |  | kwh
% of HVAC units of Total Con.(LT) |  |  | %
Total Chillers Units |  |  | kwh
% of Chillers Units of Total Con.(LT) |  |  | %
Total Lighting Units |  |  | kwh
% of Lighting Units of Total Con.(LT) |  |  | %
Total power Units |  |  | Kwh
% of power Units of Total Con.(LT) |  |  | %
Total mansion power Units |  |  | Kwh
% of M,sion power Units of Total Con.(LT) |  |  | %
Total fire & em, power Units |  |  | Kwh
% of fire & em power Units of Total Con.(LT) |  |  | %
Running Hrs | [7 empty] | 0
DG Set - 1 |  |  | hr
DG Set - 2 |  |  | hr
Chiller - 1 |  |  | hr
Chiller - 2 |  |  | hr
Chiller - 3 |  |  | hr
Chiller - 4 |  |  | hr
Steam Boiler -1 |  |  | hr
Steam Boiler -2 |  |  | hr
Steam Boiler -3 |  |  | hr
Hot Water Generator -1 |  |  | hr
Hot Water Generator -2 |  |  | hr

## Sheet2
Daily Utility Consumption Report
Prepaired by- Devendra | 2019-04-30 | occupancy | 66.34% |  |  | Occupancy% | Electricity | Water | Gas
|  | Avg temp | 32 | Last year same month avg |  | 0% | 0 | 0 | 0
|  | humidity | 71%
Description |  |  | Unit | Yesterday | Today | units.consum | MTD | Budgeted | Average/Day
ELECTRICAL CONSUMPTION
BEST Supply 11KV |  |  | kwh | 308857 | 3615871.9 | 3307014.9 | 3770894.9 | 12000 | 125696.4967
Transformer - 1 - 2500KVA |  |  | kwh | 1439384 | 2288314.7 | 848930.7 | 1297600.7 | -113696.4967 | 43253.3567
Transformer - 2 -2500KVA |  |  | kwh | 2322.58 | 1226059.4 | 1223736.82 | 1223736.82 |  | 40791.2273
DG set- 1 - 1425KVA |  |  | kwh | 37000 | 33860 | -3140 | -3140 |  | -104.6667
DG set- 2 - 1425KVA |  |  | kwh | 40010 | 3760 | 0 | 0 |  | 0
SubTotal | [5 empty] | 2069527.52 | 2503676.52 | 1237487.38 | 83455.884
GAS CONSUMPTION
Gas consumption |  |  | m3 | 1683400 | 1040573.68 | -642826.32 | -630083.32 | 800 | -21002.7773
21802.7773
WATER CONSUMPTION
Tankers |  |  | KL | 6 | 24 | 240 | 1420 | 65 | 47.3333
BMC |  |  | KL | 139493 | 99778 | -39715 | -38034 |  | -1267.8
Total water | [5 empty] | -39475 | -36614 | -1285.4667 | -1220.4667
DIESEL CONSUMPTION
Boiler House (H.S.D) |  |  | L | 2970 | 2010 | -960 | -960 |  | -32
D-G Set (H.S.D) |  |  | L | 2000 | 2075 | 0 | 0 |  | 0
Total HSD (H.S.D.) Stock |  |  | L | 4970 | 4085 | 0 | 0 |  | 0
TOTAL CONSUMPTION UNIT &COST
Utilities |  |  | Units | Cost/Unit
Electricity |  |  | kwh | 3307014.9 | 10.86 | 35914181.814 | #REF! |  | #REF!
C.N.G |  |  | Cu.Mtr | -642826.32 | 44 | -28284358.08 | #REF! |  | #REF!
H.S.D |  |  | Ltr | 0 | 61.32 | 0 | #REF! |  | #REF!
Water |  |  | Kl | -39475 | 95 | -3750125 | #REF! |  | #REF!
Total cost | [5 empty] | 3879698.734 | #REF! |  | #REF!
BRANCH READINGS & CONSUMPTION
Transformer No 1 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 945766 | 0 | -945766 | -886459 |  | -29548.6333
Main Panel BALLROOM LVL-2 -2000A |  |  | kwh | 347065 | 694322.47 | 347257.47 | 349714.47 |  | 11657.149
Fire Emergency Power Panel - 1000A |  |  | kwh | 131674 | 392708.87 | 261034.87 | 297483.87 |  | 9916.129
Main Power Panel -1600A |  |  | kwh | 153825 | 675505.75 | 521680.75 | 555909.75 |  | 18530.325
Main Lighting and Small power Panel |  |  | kwh | 303589 | 2497766.1 | 2194177.1 | 2251113.1 |  | 75037.1033
Capacitor Bank -1 1100KVAR- 2500A |  |  | kwh | 889 | 0 | -889 | -0.23 |  | -0.0076667
Chiller No 1 |  |  | kwh | 240478 | 1138016.5 | 897538.5 | 956488.5 |  | 31882.95
Chiller No 2- |  |  | kwh | 59199 | 1251783.8 | 1192584.8 | 1192583.8 |  | 39752.7933
Chiller Water pump Panel- 630A |  |  | kwh | 1037660 | 1479848.9 | 442188.9 | 505890.9 |  | 16863.03
Co-Genrator |  |  | kwh | 0 | 900 | 900 | 900 |  | 30
Lawn Pantry |  |  | kwh | 614 | 945 | 331 | 945 |  | 31.5
Pavilion Power |  |  | kwh | 187 | 375 | 188 | 374.95 |  | 12.4983
Sub Total | [5 empty] | 4911226.39 | 5224945.6 |  | 174164.8533
Transformer No 2 (Sub Feeders)
Main HVAC Power Panel- 800A |  |  | kwh | 260732.13 | 793704.71 | 532972.58 | 532972.58 |  | 17765.7527
Main MV PanelBALLROOM LVL-1- 2000A |  |  | kwh | 500726 | 707853.75 | 207127.75 | 232378.75 |  | 7745.9583
Fire Emergency Power Panel - 1000A |  |  | kwh | 144639.87 | 552102.07 | 407462.2 | 407462.07 |  | 13582.069
Main Power Panel -1800A |  |  | kwh | 539606.07 | 1244061 | 704454.93 | 704454.93 |  | 23481.831
Main Lighting and Small power Panel |  |  | kwh | 431514 | 495803.59 | 64289.59 | 78993.59 |  | 2633.1197
Capacitor Bank -2 1200KVAR- 2500A |  |  | kwh | 13596 | 55471.01 | 41875.01 | 47709.01 |  | 1590.3003
Chiller No -3 - 1200A |  |  | kwh | 68111 | 741511.59 | 673400.59 | 741511.59 |  | 24717.053
Chiller No-4 - 1200A |  |  | Kwh | 606023 | 334966 | -271057 | -254322.36 |  | -8477.412
Chiller Water pump Panel- 630A |  |  | kwh | 7711 | 0 | -7711 | -7711 |  | -257.0333
B2-Loundry power panel |  |  | kwh | 49264 | 2065.95 | -47198.05 | -44651.05 |  | -1488.3683
Sub Total | [5 empty] | 2305616.6 | 2438798.18 | -3909828.09 | 81293.2727
|  |  | Total TR1 & TR2 |  |  | 7216842.99 | 7665327.67 | -5147315.47 | 255510.9223
Floor lighting & Power consumption
2nd floor plant room |  |  | KWh | 20419 | 55085 | 34666 | 34666.182 |  | 1155.5394
5th floor spa |  |  | KWh | 2468 | 113360.74 | 110892.74 | 111001.74 |  | 3700.058
5th Floor |  |  | KWh | 159553 | 274089 | 114536 | 120790 |  | 4026.3333
12th Floor |  |  | KWh | 160561 | 218102.43 | 57541.43 | 63503.43 |  | 2116.781
20th Floor |  |  | KWh | 56221 | 7977.92 | -48243.08 | -40593.08 |  | -1353.1027
27th Floor |  |  | KWh | 251244 | 350190.03 | 98946.03 | 107016.03 |  | 3567.201
34th Floor |  |  | KWh | 85321 | 0 | -85321 | -85321 |  | -2844.0333
Sanqi |  |  | KWh | 81507 | 156094.09 | 74587.09 | 77100.09 |  | 2570.003
Consumption of Extra AHU run |  |  | KWh |  |  |  | 0
Kitchen consumption
Main kitchen power panel no 1 |  |  | KWh | 855817 | 788748 | -67069 | -66724 |  | -2224.1333
Main kitchen power panel no 2 |  |  | KWh | 885935 | 883770 | -2165 | -1926 |  | -64.2
Prato kitchen power panel |  |  | KWh | 2573 | 783142 | 780569 | 780863 |  | 26028.7667
San- Qi Indian Kitchen |  |  | KWh | 12561 | 641404 | 628843 | 630434 |  | 21014.4667
San- Qi Japanese Kitchen |  |  | KWh | 7308 | 615603 | 608295 | 609886.05 |  | 20329.535
The club kitchen |  |  | KWh | 702750 | 669905 | -32845 | -31657 |  | -1055.2333
AER Kitchen |  |  | KWh | 672760 | 487314 | -185446 | -182711 |  | -6090.3667
COLD ROOM'S |  |  | KWh | 830691 | 677157 | -153534 | -150574 |  | -5019.1333
Ball Room 1 kitchen |  |  | KWh | 526918 | 341072.6 | -185845.4 | -178388.4 |  | -5946.28
Ball Room 2 kitchen |  |  | KWh | 638711 | 407588.2 | -231122.8 | -228889.8 |  | -7629.66
B1 Laundry |  |  | kwh | 108123 | 72586.12 | -35536.88 | -35025.88 |  | -1167.5293
STP Electrical |  |  | kwh | 20089 | 725847 | 705758 | 711076 |  | 23702.5333
Cooling Tower |  |  | kwh | 498687 | 960770 | 462083 | 480637 |  | 16021.2333
Total | [5 empty] | 2291983.92 | 2340508.92 |  | 78016.964
WATER
R.o.plant |  |  | KL | 245378 | 175511 | -69867 | -68913 |  | -2297.1
STP Water Prod |  |  | KL | 185930 | 60336 | -125594 | -123195 |  | -4106.5
Total water Produce |  |  |  | 3 |  | -195461 | -192255 |  | -6408.5
Domestic Zone-1 |  |  | KL | 414191 | 351186 | -63005 | -61700 |  | -2056.6667
Domestic Zone-2 |  |  | KL | 72 | 84 | 12 | 292 |  | 9.7333
Domestic Zone-3 |  |  | KL | 97897 | 82333 | -15564 | -15094 |  | -503.1333
Flush Zone -1 |  |  | KL | 149846 | 115948 | -33898 | -33585 |  | -1119.5
Flush Zone -2 |  |  | KL | 7356 | 2658 | -4698 | -4527 |  | -150.9
Flush Zone -3 |  |  | KL | 5372 | 2507 | -2865 | -2631 |  | -87.7
Total water consum | [5 empty] | -120018 | -117245 |  | -3908.1667
GAS Branch CONSUMPTION
H.W.G. Gas meter reading |  |  | m3 | 831972 | 650192.71 | -181779.29 | -175895.75 |  | -5863.1917
Prato Kitchen Gas meter Reading |  |  | m3 | 73583 | 51370 | -22213 | -22213.4 |  | -740.4467
BallRoom Gas |  |  | m3 | 146368 | 83294.49 | -63073.51 | -61392.95 |  | -2046.4317
Sanqi IndianGas meter Reading |  |  | m3 | 31404 | 39666 | 8262 | 8262 |  | 275.4
Sanqi Japanese Gas meter Reading |  |  | m3 | 8971 | 6221.3 | -2749.7 | -2748.4 |  | -91.6133
Percentag of ele, unit per area
Total HVAC units |  |  | kwh |  |  | 21684.48 | 144404.48 |  | 4813.4827
% of HVAC units of Total Con.(LT) |  |  | % |  |  | 0.6557% | 7.6813 |  | 0.25604
Total Chillers Units |  |  | kwh |  |  | 2492466.89 | 2636261.42 |  | 87875.3807
% of Chillers Units of Total Con.(LT) |  |  | % |  |  | 75.37% | 9.7577 |  | 0.32526
Total Lighting Units |  |  | kwh |  |  | 2258466.69 | 2330629.69 |  | 77687.6563
% of Lighting Units of Total Con.(LT) |  |  | % |  |  | 68.29% | 5.1968 |  | 0.17323
Total power Units |  |  | Kwh |  |  | 1226135.68 | 1260364.75 |  | 42012.1583
% of power Units of Total Con.(LT) |  |  | % |  |  | 37.08% | 2.5149 |  | 0.08383
Total mansion power Units |  |  | Kwh |  |  | 554385.22 | 583032.22 |  | 19434.4073
% of M,sion power Units of Total Con.(LT) |  |  | % |  |  | 16.76% | 1.9552 |  | 0.065173
Total fire & em, power Units |  |  | Kwh |  |  | 668497.07 | 704945.94 |  | 23498.198
% of fire & em power Units of Total Con.(LT) |  |  | % |  |  | 20.21% | 2.488 |  | 0.082935
Running Hrs
DG Set - 1 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
DG Set - 2 |  |  | hr | 0 | 0 | 0 | 0 |  | 0
Chiller - 1 |  |  | hr | 40059 | 36196 | -3863 | -3550.48 |  | -118.3493
Chiller - 2 |  |  | hr | 300 | 32397.32 | 32097.32 | 32097.32 | 28234.32 | 1069.9107
Chiller - 3 |  |  | hr | 41730 | 30495.25 | -11234.75 | -11163.14 |  | -372.1047
Chiller - 4 |  |  | hr | 32667.24 | 25683.26 | -6983.98 | -6886.67 |  | -229.5557
Steam Boiler -1 |  |  | hr | 22799 | 21285.49 | -1513.51 | -1454.1 | -19732.24 | -48.47
Steam Boiler -2 |  |  | hr | 25052 | 22354.72 | -2697.28 | -2689 |  | -89.6333
Steam Boiler -3 |  |  | hr | 70402 | 64789.37 | -5612.63 | -5574.73 | -8309.91 | -185.8243
Hot Water Generator -1 |  |  | hr | 1839.44 | 17.9 | -1821.54 | -1598.96 |  | -53.2987
Hot Water Generator -2 |  |  | hr | 4637 | 603.07 | -4033.93 | -4033.93 |  | -134.4643

## Sheet3
15988
15961
16029
16163
15754